## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | Translation and QA Only | 14 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Dirty Utility, 14m² provides a space for the decontamination and storage of bedpans, urinals and bowls, testing and disposal of patient specimens, disposal of clinical and other wastes, cleaning and holding of used equipment for collection, and holding of soiled linen for collection. The Dirty Utility, 14m2 may provide access doors from both sides of the room. Note: due to the availability of washers that do not require pre-handling of items a spray hose and flushing rim sink are no longer included in the Dirty Utility, 14m² fit out. |  | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005] pull handle/push plate, closer
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 2 | [DWGL-005] pull handle/push plate, closer
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to room side
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 1 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 2 | 1 |  | [FIDI-001]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FIHR-029 | HOOK: equipment, wall mounted | 2 | 3 |  | [FIHR-029] optional, for clean linen bags
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FIHR-131 | HOOK: catheter bag, wall mounted | 2 | 3 |  | [FIHR-025] optional
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FIHR-141 | RACK: bed pan, wall mounted | 1 | 1 |  | [FIHR-038] quantity to be based on service requirements
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FIHR-144 | RACK: urinal/bottle, wall mounted | 1 | 1 |  | [FIHR-053] quantity to be based on service requirements
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 3 | 1 |  | [MMGE-048]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FQWS-058 | BIN: general waste, 240L | 1 | 1 |  | [FQCW-017] type, size and quantity of bins to be determined based on service requirements and waste management policies
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | FQWS-238 | BIN: clinical waste, 240L | 1 | 1 |  | [FQCW-006] type, size and quantity of bins to be determined based on service requirements and waste management policies
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | HYBA-301 | SINK: single bowl | 1 | 1 |  | [HYBA-052] hot water
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | HYTP-062 | TAPWARE: basin, tap set, fixture mounted, lever handles | 1 | 1 |  | [HYTP-038] to sink
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 1 | 1 |  | [FIJO-021] with wet edge
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | JOBE-231 | BENCH SUPPORT: legs and frame, stainless steel | 1 | 1 |  | [FIJO-100]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | MMIC-361 | WASHER SANITISER: pan | 1 | 1 |  | [MMIC-095] combined utensil/pan sanitiser may be provided
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | MMIC-362 | WASHER SANITISER: utensil | 1 | 1 |  | [MMIC-097] combined utensil/pan sanitiser may be provided
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | MMLA-013 | DEVICE: analyser, urinalysis | 1 | 3 |  | [MMLA-013] optional
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FFE | JOBE-232 | BENCH SUPPORT: legs and frame, stainless steel, with low shelf | 1 | 1 |  | [FIJO-196] + [FIJO-197]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FIN | CLTI-025.02 | CEILING: drop-in tiles, moisture resistant, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-014]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 6 | 1 | Floor Skirting | [FLSK-010]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 1 | [FLVY-009]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 6 | 1 | Wall Finish 2 | [WLWA-023]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | ELGP-191 | GPO: single, special, for equipment, wall mounted | 2 | 1 |  | [ELGP-106] for washer sanitisers
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | ELGP-301 | ISOLATOR: one phase, wall mounted | 1 | 1 |  | [ELPR-003]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-010]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | HYDR-101 | TUNDISH: fixture mounted | 1 | 3 |  | [HYDR-006] optional, dependent on machine requirements
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | HYGE-181 | VALVE: backflow prevention, wall recessed | 1 | 1 |  | [HYGE-028]
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | HYTP-431 | OUTLET: water, cold | 2 | 1 |  | [HYTP-008] for washer sanitisers
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | HYTP-432 | OUTLET: water, hot | 2 | 1 |  | [HYTP-013] for washer sanitisers
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | [ITIN-016] optional, for urinalysis machine
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 2 | 1 |  | 1 to sink, 1 to basin
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to sink tapware, 1 to basin tapware
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 1 | 1 |  | to sink tapware
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
DTUR-14 | Dirty Utility, 14m2 | Clinical Support Set 3 | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109.1] optional, for urinalysis machine