## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | Translation and QA Only | 12 | 2700 |  | 5 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 staff intermittently | The Equipment Clean Up Room is used for cleaning of equipment used in patient care or loaned to outpatients following return. | ~ Storage will be required for holding cleaning equipment. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | D+W | DOHI-017.01 | DOOR: hinged, 1 leaf, 1100 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-020] lockable
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-006] to room side
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | FIDI-111 | DISPENSER: PPE, disposable gowns/aprons, wall mounted | 1 | 1 |  | [FIDI-018]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 3 |  | [FIDI-001] Optional
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | FIDI-271 | DISPENSER: moisturiser, wall mounted | 1 | 3 |  | [FIDI-022] optional
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | FIDI-291 | DISPENSER: laundry detergent, wall mounted | 1 | 1 |  | [FIDI-008] To sink.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | FIGE-009 | PLATFORM: equipment washing, wall mounted | 1 | 1 |  | [FIGE-009] Stainless steel, grated, height adjustable, wall mounted.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 3 |  | [HYBA-010] Refer to BHWS-B (similar). Elbow action levers or handsfree optional.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | HYBA-301 | SINK: single bowl | 1 | 1 |  | [HYBA-055] hot water
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | HYGE-151 | HOSE REEL: retractable | 1 | 1 |  | [HYTP-003]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 3 |  | [HYTP-037] to basin. Elbow action levers or handsfree optional.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 1 | 1 |  | [FIJO-021] Wet edge and inset sink/s. Length to suit layout, refer RLS or project specific requirements.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | JOCU-021 | CUPBOARD: tall, double door | 1 | 3 |  | [FIJO-117] Optional. Number to suit layout.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 2 | 1 |  | [FIJO-152] Over bench. Number to suit layout, refer RLS or project specific requirements.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | MMTR-071 | TROLLEY: equipment, 490W x 490D x 900H nom | 1 | 3 |  | [MMGE-119] Optional.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | JOBE-232 | BENCH SUPPORT: legs and frame, stainless steel, with low shelf | 1 | 1 |  | [FIJO-197] shelf at 350mm AFFL or underbench, stainless steel cupboard.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FFE | HYTP-236 | TAPWARE: sink, spray hose, hand-held, connection and bracket on wall | 1 | 3 |  | [HYTP-006] above sink, optional. Depends on operational/infection control policies.
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-009]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FIN | FLVY-112 | FLOOR FINISH: vinyl, seamless, non-slip, safety | 1 | 1 | Floor Finish 1 | [FLVY-004]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-020]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 1 | 1 |  | [ELGP-208]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004] to wash bay
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | SER | HYTP-431 | OUTLET: water, cold | 2 | 1 |  | [HYTP-008] hose reel and spray hose connection
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | SER | HYTP-432 | OUTLET: water, hot | 2 | 1 |  | [HYTP-013] hose reel and spray hose connection
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to sink
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to sink tapware
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 1 | 1 |  | to sink tapware
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | Clinical Support Set 3 | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 3 |  | optional; to spray hose if provided