## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
ECL-8 | Equipment Clean-Up, 8m2 | 8 |  | 1 - 2 | 24 Hours |  | The Equipment Clean-Up Room is used for cleaning and maintaining of equipment used in the Unit. Storage may be required for holding cleaned equipment and spares. Equipment may also be recharged in this room. Natural light is desirable.

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
ECL-8 | Equipment Clean-Up, 8m2 | FE | FE-2800 | Basin - handwash, Type B | 1 | Refer to BHWS-B (sim) |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ECL-8 | Equipment Clean-Up, 8m2 | FE | FE-49000 | Sink - 500x450x250D | 2 | hot water |  |  |  | No | No | Yes | Yes | Yes | Yes | Yes | No | No
ECL-8 | Equipment Clean-Up, 8m2 | FE | FE-4045 | Tapware - elbow mixer | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | FF | FF-1010 | Bench - stainless steel | 1 | with wet edge, inset sink |  |  |  | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | FF | FF-19820 | Shelf - SS, under | 1 | under bench |  |  |  | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | FF | FF-20000 | Shelving unit - adjustable | 1 | over bench |  |  |  | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | FF | FF-4360 | Cupboard - door ht adj. shelves | 1 | lockable, optional |  |  |  | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | FF | FF-6152 | Dispenser - disposable glove | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | FF | FF-6154 | Dispenser - paper/ hand towel | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | FF | FF-6156 | Dispenser - soap | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | FF | FF-6158 | Dispenser - soap antiseptic | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | FF | FF-5824 | Waste bin - general | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | SE | S-9001 | GPO: Double | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | SE | S-4033 | Floor waste | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | SE | S-5015 | Ventilation | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | SE | S-5019 | Exhaust | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | SE | S-6000 | General fluorescent | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | SE | S-6200 | Light switches | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | Fabrics | 1020 | Floor finish | 1 |  | Vinyl, non-slip | Safety | Seamless, coved | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | Fabrics | 3052 | Wall finish | 1 |  | Vinyl | Prefinished | Wall vinyl to 1500 AFFL | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | Fabrics | 5021 | Ceiling - Plasterboard | 1 |  | Plasterboard | Paint, washable | Water resistant, flush set, suspended | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | Fabrics | 8010 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | Fabrics | 8040 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | Fabrics | 9004 | Door - 1100mm | 1 | 1100mm clear opening, lockable | Solid Core/ Glass | Paint | Single leaf, observation panel | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
ECL-8 | Equipment Clean-Up, 8m2 | Fabrics | 2000 | Skirting | 1 |  | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No