## Room Data
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Acoustics | Description / Special Requirements
ENPR | Procedure Room - Endoscopy | 45 | 24 Hours | 1 patient; 5 - 8 staff |  | The Procedure Room - Endoscopy provides an aseptic environment in which to carry out endoscopic procedures under sedation and general anaesthetic. The Procedure Room may be used for specialities including ENT, Urology, Endoscopy and any other similar procedures. The Procedure Room will have direct access to a reprocessing area (or route to reprocessing area) and, in some models, a sterile stock. Additional Design Considerations: Minimum critical dimension 6500mm. Lead shielding may be required depending on use of X-ray equipment - to be assessed by Radiation Consultant. External windows are desirable - double glazed with integral venetian blinds. Provide isolated power supply individually to each pendant, together with its associated line isolation and overload monitors. Dimmable lighting is required. If the room is used for Bronchoscopy procedures, negative pressure air conditioning and direct exhaust to roof is required.

## Items
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
ENPR | Procedure Room - Endoscopy | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FA | CLFS-005 | CEILING: plasterboard, flush set, suspended, paint, scrub resistant | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FA | DWGL-011 | DOOR: 950mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | auto release, delayed action | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FA | DWGL-051 | DOOR: 1600mm c/o, double leaf, observation panel, solid core/glass, paint | 1 | auto release, delayed action - check height of doors against major transferable equipment, eg. image intensifier | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 4 | optional | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FA | DWPR-011 | DOOR PROTECTION: protection plate, to full height | 3 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | DWWH-007 | SHUTTER: for observation panel, magnetic flap for laser protection | 3 | optional - if lasers in use | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ELBO-003 | CONTROL PANEL: lighting | 2 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ELBO-009 | SWITCH: "Laser in use" | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ELBO-016 | SWITCH: "X-Ray in use" | 1 | optional | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ELGP-121 | GPO: emergency power, single, on pendant | 8 | on pendant 1 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ELGP-121 | GPO: emergency power, single, on pendant | 8 | on pendant 2 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 2 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ELGP-132 | GPO: UPS, single, on pendant | 4 | on pendant 1 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ELGP-132 | GPO: UPS, single, on pendant | 4 | on pendant 2 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 3 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ELPR-004 | MONITOR: line isolation | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ELPR-006 | RCD: residual current device | 3 | 1 to wall mounted services panel. LIM to be provided to UPS outlets only | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ELPR-007 | UPS: status indicator | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ELPR-007 | UPS: status indicator | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 2 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | FIDI-014 | DISPENSER: disposable glove | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | FIDI-017 | DISPENSER: goggles | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | FIDI-030 | DISPENSER: soap | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | FIHR-064 | BRACKET: for display screen, arm mounted, rotating | 1 | attached to MMSP-035 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | FIHR-066 | BRACKET: for display screen, wall mounted, articulated, adj height | 1 | At write up bench | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | FIJO-013 | BENCH: 450D, open under, stainless steel | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | FIJO-100 | BENCH LEGS: stainless steel, for bench top | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | FIJO-212 | BULKHEAD: joinery | 2 | plasterboard bulkhead is an optional alternative | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | FIJO-214 | CUPBOARD: tall, double door, glazed, adj shelves, lockable | 3 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FA | FLVY-004 | FLOOR FINISH: vinyl, seamless, coved, non-slip, safety | 1 | under basin | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | FQSM-039 | TROLLEY: waste bag | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | HYBA-009 | BASIN: handwash, Type A, scrub | 1 |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENPR | Procedure Room - Endoscopy | FFE | HYTP-042 | TAPWARE: sensor | 1 |  | No | No | Yes | No | Yes | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | ITAV-057 | SPEAKER: ceiling recessed | 2 | supplied with DOR system, optional | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | ITAV-060 | CONTROL PANEL: AV integration system, wall mount | 1 | supplied with DOR system | Yes | Yes | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ITCL-005 | BUTTON: nurse call, orderly / porter | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ITCL-005 | BUTTON: nurse call, orderly / porter | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | ITCL-012 | CAMERA: observation | 1 | supplied with DOR system, optional | Yes | Yes | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | ITCL-020 | CLOCK: clock system slave, dual digital / elapsed time | 1 |  | Yes | Yes | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ITCL-023 | CONTROL PANEL: master clock system | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ITIN-014 | OUTLET: data, single RJ45, on pendant | 4 | on pendant 1 | No | Yes | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ITIN-014 | OUTLET: data, single RJ45, on pendant | 4 | on pendant 2 | No | Yes | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ITIN-023 | OUTLET: data, double RJ45, on data/ AV panel | 1 |  | No | Yes | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 |  | No | Yes | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ITIN-063 | OUTLET: HDMI, on data/ AV panel | 1 |  | No | Yes | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | ITIN-120 | PATCH PANEL: data integration | 1 | supplied with DOR system | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ITIN-140 | DATA PANEL: data / AV outlets, ceiling mounted | 1 | or pendant mounted; for endoscopy tower | No | Yes | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 1 |  | Yes | Yes | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | ITNE-050 | TELEPHONE: handset, desktop, handsfree | 1 | to bench | No | Yes | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | ITNE-052 | TELEPHONE: handset, wall mount | 1 |  | No | Yes | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | ITNE-066 | COMPUTER: all-in-one, wall mounted | 1 |  | Yes | Yes | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 2 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 2 | wording on lights subject to jurisdictional legislation - external to room, delete from list if listed in the adjacent room | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | LIFX-003 | LIGHT: illuminated sign, "Laser in Use" | 2 | optional - external to room, delete from list if listed in the adjacent room | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | LIPO-006 | LIGHT: examination, mobile | 1 |  | Yes | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MEEX-008 | EXHAUST: low level | 1 | for removal of anaes. gases - rectilinear or triangular duct can optionally be provided | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-004 | OUTLET: carbon dioxide (CO2), on pendant | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-004 | OUTLET: carbon dioxide (CO2), on pendant | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-021 | OUTLET: medical air (MA), on pendant | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-021 | OUTLET: medical air (MA), on pendant | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-041 | OUTLET: oxygen (O2), on pendant | 2 | on pendant 1 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-041 | OUTLET: oxygen (O2), on pendant | 2 | on pendant 2 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-051 | OUTLET: scavenge, on pendant | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-051 | OUTLET: scavenge, on pendant | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-061 | OUTLET: suction, on pendant | 3 | on pendant 1 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-061 | OUTLET: suction, on pendant | 3 | on pendant 2 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGFP-001 | ALARM PANEL: medical gases | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MGFP-002 | FLOWMETER: medical air | 2 | for outlets on pendants | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MGFP-004 | FLOWMETER: oxygen | 4 | for outlets on pendants | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMBE-044 | TROLLEY: patient, transport | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMGE-002 | ADAPTER: suction | 6 | for outlets on pendants | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMGE-014 | CHAIR: anaesthetist | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMGE-045 | IV STAND: mobile | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMGE-078 | PUMP: infusion | 1 |  | Yes | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMGE-088 | SAFE: dangerous drugs, small | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMGE-122 | TROLLEY: gowns | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMGE-123 | TROLLEY: instrument | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMGE-142 | TROLLEY: sharps bin | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMGE-167 | CHAIR: surgeon | 2 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMGE-168 | STAND: infusion pump, mobile | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMIC-010 | CABINET: endoscope, drying & storage, pass-through filtered / forced air drying | 1 | optional | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMOP-028 | KICKBUCKET & STAND | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMOP-040 | MACHINE: anaesthetic | 1 | recommended to be with integral monitors | Yes | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMOP-043 | MACHINE: electrosurgical, diathermy | 1 |  | Yes | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMOP-069 | STAND: bowl, single | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMOP-076 | TABLE: mayo | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMOP-085 | TROLLEY: anaesthetic | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMOP-087 | TROLLEY: endoscope | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMOP-088 | TROLLEY: endoscopic, equipment | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMOP-096 | DISPLAY SCREEN: AV integration | 1 | supplied with DOR system, 60" LCD screen for image display | Yes | Yes | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMOP-096 | DISPLAY SCREEN: AV integration | 1 | supplied with DOR system, on pendant arm | Yes | Yes | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMOP-103 | SYSTEM: digital integration in operating rooms (DOR) | 1 | IT and AV system with associated equipment; servers located outside entry to room | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 | flush mounted | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMSP-034 | PENDANT: single, dual arm, surgical & anaesthetic combined (fixed or adjustable height) | 2 |  | Yes | Yes | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FFE | MMSP-035 | PENDANT: single, dual arm, display screen | 1 | camera ready | Yes | Yes | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 |  | No | No | No | No | No | No | No | No | No