## Room Template Data
Procedure Room - Endoscopy (ENPR) - Room Template Properties and Room Template Data
2026-08-06
No. of Standard Components = 1
Code | Template Name | Standard Area | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Briefing - Hours of Operation - Duration - Duration | Briefing - Hours of Operation - Duration - extended/limited hours | Briefing - Hours of Operation - Hours/days - Open time | Briefing - Hours of Operation - Hours/days - Close time | Briefing - Hours of Operation - Hours/days - Days | Briefing - Hours of Operation - Comment | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experiance system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statuatory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magentic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: sensitive | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
ENPR | Procedure Room - Endoscopy | 45 |  | 2 | 06.05.2025 | 24 hours | 0 |  |  |  |  | 1 patient; 5-8 staff | A Procedure Room - Endoscopy provides an aseptic environment in which to carry out endoscopic procedures on a patient under local, regional or general anaesthetic. The Procedure Room may be used for specialties including ENT, urology, endoscopy and other similar procedures. The Procedure Room may have direct access to a reprocessing area and, in some models, a sterile stock. | ~ The minimum critical dimension centred on the procedure zone is 6400mm clear to ensure adequate space for the procedure, circulation and equipment storage. ~ Isolated power supply is required individually to each medical services pendant, together with its associated line isolation and overload monitors. ~ Location and quantity of RCD outlets to suit overall electrical service provision and is to be confirmed by the project to suit local engineering services guidelines/policies. ~ If the room is used for Bronchoscopy procedures, negative pressure air conditioning and direct exhaust to roof is required. ~ If the room is used for bronchoscopy procedures, negative pressure air conditioning and direct exhaust to outside is required. ~ Provision of reticulated nitrous oxide is optional and must be conﬁrmed to suit local jurisdictional policies and operational service requirements. The use of nitrous oxide in operating theatres and procedural suites and emergency departments is declining due to a range of clinical and environmental concerns. Reticulated systems have been found to increase leakage of nitrous oxide (a potent greenhouse gas) to atmosphere, can increase facility operating costs and potentially expose staff to nitrous oxide. Reticulated nitrous oxide and associated scavenge outlets are not mandatory for any healthcare service and point of care cylinders can meet clinical requirements for the majority of healthcare facilities. Due consideration must be given to a range of operational considerations including monitoring and measurement of usage, management of leakage, WHS requirements relating to the use of cylinders, approach to the provision of scavenge where cylinders are used, appropriate storage for cylinders, and security of gas sources given it is used as a recreational drug. ~ If laser equipment is to be used, ‘laser in use’ warning lights are required outside all entry doors to the room. ~ If x-ray equipment is to be used, ‘x-ray in use’ warning lights are required outside all entry doors to the room. Radiation shielding will also be required and is to be assessed by a Radiation Consultant. ~ Automated doors with motion or elbow activation are provided to the Procedure Room - Endoscopy from the corridor and reprocessing areas. Buttons/sensors should be appropriately located in relation to the door, including consideration for approach and movement of patients on beds and mobile equipment. 2-gang buttons that support the opening of either one or both leaves of the door as required are desirable. ~ Height of doors to be confirmed to suit the movement of mobile equipment such as mobile imaging devices. ~ If external windows are provided, they are to be double glazed with integral venetian blinds (with either manual or automated controls). ~ Room lights to be dimmable. Lighting control to room rights, warning signs, and operating lights to be coordinated within the room and an appropriate lighting control panel to be provided to functional requirements. ~ Configuration of services pendant (horizontal or vertical) to suit services requirements. Accessories (e.g. shelves, drawers, rails, etc.) are optional and can be selected to suit service and equipment requirements. Services allocations are indicative - type and number of services on the pendant to suit service requirements ~ Services pendant arms to have an adequate reach to be moved out of the way to allow for adequate room for movement of a patient trolley and mobile equipment. | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE
This shape represents a table slicer. Table slicers are not supported in this version of Excel.
If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Items In Room Template
Standard Components - Items in Room Template
2026-08-06
No. of Standard Components = 1
Code | Template Name | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
ENPR | Procedure Room - Endoscopy | D+W | AHDEC-031 | SWITCH: door release, single gang, automatic door, wall mounted | 1 | 1 | Internal - Door 3
ENPR | Procedure Room - Endoscopy | D+W | AHDEC-031 | SWITCH: door release, single gang, automatic door, wall mounted | 1 | 1 | Internal - Door 2
ENPR | Procedure Room - Endoscopy | D+W | AHDEC-036 | SWITCH: door release, double gang, automatic door, wall mounted | 1 | 1 | Internal - Door 1 | to allow for opening either one or both leaves of the door
ENPR | Procedure Room - Endoscopy | D+W | AHDMO-001 | DOOR MOTORISATION: swing | 1 | 1 | Internal - Door 1 | delayed action closing
ENPR | Procedure Room - Endoscopy | D+W | AHDMO-001 | DOOR MOTORISATION: swing | 1 | 1 | Internal - Door 3
ENPR | Procedure Room - Endoscopy | D+W | AHDMO-001 | DOOR MOTORISATION: swing | 1 | 1 | Internal - Door 2
ENPR | Procedure Room - Endoscopy | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 1 | to both sides
ENPR | Procedure Room - Endoscopy | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 3 | to both sides
ENPR | Procedure Room - Endoscopy | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 2 | to both sides
ENPR | Procedure Room - Endoscopy | D+W | DOHI-014.03 | DOOR: hinged, 1 leaf, 950 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 3 | optional - to dirty scope room if floor plan supports direct access
ENPR | Procedure Room - Endoscopy | D+W | DOHI-014.03 | DOOR: hinged, 1 leaf, 950 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 2 | optional - to clean scope room if floor plan supports direct access
ENPR | Procedure Room - Endoscopy | D+W | DOHI-212.03 | DOOR: hinged, 2 leaves, 1600 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 1 | to corridor, cover required to vision panel if laser is to be used
ENPR | Procedure Room - Endoscopy | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 2 | 1
ENPR | Procedure Room - Endoscopy | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 2 | 1
ENPR | Procedure Room - Endoscopy | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 2 | 1
ENPR | Procedure Room - Endoscopy | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 2 | 1
ENPR | Procedure Room - Endoscopy | FFE | FIHR-212 | BRACKET: computer display screen, single, articulated, wall mounted | 1 | 1 |  | to workstation for digital operating room (DOR) computer
ENPR | Procedure Room - Endoscopy | FFE | FIHR-327 | BRACKET: keyboard and mouse, articulated, wall mounted | 1 | 1 |  | to workstation for digital operating room (DOR) computer
ENPR | Procedure Room - Endoscopy | FFE | FIHR-331 | BRACKET: television/AV system display screen, single, fixed, wall mounted | 1 | 1 |  | to digital operating room (DOR) display screen
ENPR | Procedure Room - Endoscopy | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | ITCL-069 | CLOCK: electric, master clock system, slave, digital, dual time/elapsed time | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 2 | 1
ENPR | Procedure Room - Endoscopy | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | ITNE-122 | COMPUTER: single display screen, all-in-one, medical grade | 1 | 1 |  | workstation for digital operating room (DOR) computer
ENPR | Procedure Room - Endoscopy | FFE | ITNE-204 | INPUT DEVICE: keyboard and mouse, wireless, medical grade, washable | 1 | 1 |  | workstation for digital operating room (DOR) computer
ENPR | Procedure Room - Endoscopy | FFE | JOCU-023 | CUPBOARD: tall, double door, glazed | 3 | 1
ENPR | Procedure Room - Endoscopy | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | plasterboard bulkhead is also acceptable
ENPR | Procedure Room - Endoscopy | FFE | MMBE-151 | TROLLEY: patient, transport | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMGE-045 | POLE: IV, mobile | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMGE-291 | DEVICE: pump, infusion, single | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMIC-301 | CABINET: endoscope, drying and storage, single door, pass-through | 1 | 1 |  | optional - to clean scope room if floor plan supports direct access, interlocking mechanisms requried
ENPR | Procedure Room - Endoscopy | FFE | MMOP-122 | STOOL: mobile, anaesthetic | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMOP-162 | MACHINE: anaesthetic, with patient monitor, high acuity | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMOP-166 | TROLLEY: anaesthetic | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMOP-171 | MACHINE: electrosurgical, diathermy | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMOP-202 | STAND: bowl, single | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMOP-211 | KICKBUCKET: with stand | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMOP-242 | CAMERA: endoscopic | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMOP-252 | DEVICE: processor, on endoscopy stack | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMOP-262 | DEVICE: light source, on endoscopy stack | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMOP-272 | DEVICE: insufflator, on endoscopy stack | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMOP-282 | TROLLEY: endoscopy stack, equipment | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMOP-297 | CONTAINER: endoscope, transport | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMOP-302 | DISPLAY SCREEN: digital operating room (DOR) integration, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMOP-311 | CAMERA: patient observation, digital operating room (DOR) integration, ceiling mounted | 1 | 1 |  | optional
ENPR | Procedure Room - Endoscopy | FFE | MMOP-331 | SPEAKER: digital operating room (DOR) integration, ceiling recessed | 2 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMOP-341 | CONTROL PANEL: digital operating room (DOR) integration, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMOP-351 | PATCH PANEL: digital room operating (DOR) integration, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMOP-371 | SYSTEM CABINET: digital integration in operating rooms (DOR) | 1 | 1 |  | located in ICT/AV cupboard (see EXIT)
ENPR | Procedure Room - Endoscopy | FFE | MMPH-001 | SAFE: dangerous drugs, wall mounted, small | 1 | 1 |  | with card reader
ENPR | Procedure Room - Endoscopy | FFE | FQWS-005 | BIN: sharps, clinical, extra large | 1 | 1 |  | on cart
ENPR | Procedure Room - Endoscopy | FFE | FQWS-032 | CART: sharps bin, clinical, foot pedal bin operation | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | FQWS-396 | TROLLEY: waste bag | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMTR-052 | TROLLEY: airway/intubation, 600W x 490D x 900H nom | 1 | 1 |  | difficult airway (DVA)
ENPR | Procedure Room - Endoscopy | FFE | MMTR-071 | TROLLEY: equipment, 490W x 490D x 900H nom | 1 | 1 |  | endoscope clean/dirty transport
ENPR | Procedure Room - Endoscopy | FFE | MMTR-072 | TROLLEY: equipment, 600W x 490D x 900H nom | 1 | 1 |  | endoscope equipment and accessories
ENPR | Procedure Room - Endoscopy | FFE | MMTR-077 | TROLLEY: instruments, 600W x 490D x 900H nom | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMTR-094 | TROLLEY: procedure, 900W x 490D x 900H nom | 1 | 1 |  | for biopsies, with drawers
ENPR | Procedure Room - Endoscopy | FFE | MMTR-096 | TROLLEY: scout, 490W x 490D x 900H nom | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMTR-108 | TROLLEY: set-up, table 1250W x 800D x 900H nom | 1 | 1 |  | with drawers
ENPR | Procedure Room - Endoscopy | FFE | MMTR-123 | TROLLEY: gowns/scrubs, 1220W x 610D x 1830H nominal | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMTR-171 | TROLLEY: mayo table | 1 | 1
ENPR | Procedure Room - Endoscopy | FFE | MMOP-123 | STOOL: mobile, surgeon | 2 | 1
ENPR | Procedure Room - Endoscopy | FIN | CLFI-003 | CEILING FINISH: paint, sterile areas | 1 | 1 | Ceiling Finish 2
ENPR | Procedure Room - Endoscopy | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
ENPR | Procedure Room - Endoscopy | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
ENPR | Procedure Room - Endoscopy | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
ENPR | Procedure Room - Endoscopy | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1 | alternative impermeable seamless materials may also be acceptable, confirm material selection to suit infection prevention and control requirements
ENPR | Procedure Room - Endoscopy | MSP | ELGP-146 | GPO: single, emergency power, on service panel | 4 | 1 | Panel 1 | quantity and type of power outlets to suit service requirements
ENPR | Procedure Room - Endoscopy | MSP | ELGP-146 | GPO: single, emergency power, on service panel | 2 | 1 | Panel 2 | quantity and type of power outlets to suit service requirements
ENPR | Procedure Room - Endoscopy | MSP | ELGP-146 | GPO: single, emergency power, on service panel | 3 | 1 | Panel 3 | quantity and type of power outlets to suit service requirements
ENPR | Procedure Room - Endoscopy | MSP | ELGP-151 | GPO: single, emergency power, on services pendant | 12 | 1 | Pendant 1 | quantity and type of power outlets to suit service requirements
ENPR | Procedure Room - Endoscopy | MSP | ELGP-176 | GPO: single, UPS, on service panel | 3 | 1 | Panel 3
ENPR | Procedure Room - Endoscopy | MSP | ELGP-181 | GPO: single, UPS, on services pendant | 4 | 1 | Pendant 1 | quantity and type of power outlets to suit service requirements
ENPR | Procedure Room - Endoscopy | MSP | ELPR-033 | PANEL: UPS status indicator, on services panel | 1 | 1 | Panel 3
ENPR | Procedure Room - Endoscopy | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 1
ENPR | Procedure Room - Endoscopy | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 2
ENPR | Procedure Room - Endoscopy | MSP | ELPR-073 | RCD: residual current device, on services panel | 2 | 1 | Panel 3
ENPR | Procedure Room - Endoscopy | MSP | ITCL-185 | BUTTON: staff assist, with cancel, on services pendant | 1 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | MSP | ITCL-195 | BUTTON: emergency, with cancel, on services pendant | 1 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | MSP | ITCL-213 | BUTTON: orderly / porter, with cancel, on services pendant | 1 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | MSP | ITIN-014 | OUTLET: data, single RJ45, on services pendant | 4 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 3 | 1 | Panel 2
ENPR | Procedure Room - Endoscopy | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 3
ENPR | Procedure Room - Endoscopy | MSP | MGAS-001 | OUTLET: carbon dioxide (CO2), on services pendant | 1 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | MSP | MGAS-002 | OUTLET: carbon dioxide (CO2), on services panel | 1 | 1 | Panel 2 | for endoscopy stack
ENPR | Procedure Room - Endoscopy | MSP | MGAS-021 | OUTLET: medical air, on services pendant | 1 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | MSP | MGAS-031 | OUTLET: nitrous oxide (N2O), on services pendant | 1 | 1 | Pendant 1 | optional; provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
ENPR | Procedure Room - Endoscopy | MSP | MGAS-041 | OUTLET: oxygen (O2), on services pendant | 2 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | MSP | MGAS-051 | OUTLET: scavenge, on services pendant | 1 | 1 | Pendant 1 | optional; provided if reticulated nitrous oxide provided - provision of reticulated nitrous oxide to be confirmed to suit project and service requirements
ENPR | Procedure Room - Endoscopy | MSP | MGAS-061 | OUTLET: suction, on services pendant | 3 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | MSP | MGFP-061 | ADAPTER: suction | 3 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | MSP | MMOP-303 | DISPLAY SCREEN: digital operating room (DOR) integration, pendant mounted | 1 | 1 | Pendant 3 - Arm 2
ENPR | Procedure Room - Endoscopy | MSP | MMOP-362 | OUTLET: digital operating room (DOR) integration, wall mounted | 1 | 1 | Panel 2 | for connection of endoscopy stack to digital operating room (DOR) system
ENPR | Procedure Room - Endoscopy | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1
ENPR | Procedure Room - Endoscopy | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2
ENPR | Procedure Room - Endoscopy | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 3
ENPR | Procedure Room - Endoscopy | MSP | MMSP-101 | MEDICAL SERVICES PENDANT: single arm, horizontal services head | 1 | 1 | Pendant 1 | ergonomic control handles required; configuration (horizontal or vertical) to suit services requirements; services allocations are indicative - type and number of services on the pendant to suit service requirements
ENPR | Procedure Room - Endoscopy | MSP | MMSP-224 | MEDICAL SERVICES PENDANT: double arm, 1 light head, operating / display screen | 1 | 1 | Pendant 3
ENPR | Procedure Room - Endoscopy | MSP | ELGP-318 | ISOLATOR: three phase, with socket outlet, on services pendant | 1 | 1 | Pendant 1 | optional - depending on equipment requirements, may be wall mounted
ENPR | Procedure Room - Endoscopy | MSP | ELPR-034 | PANEL: UPS status indicator, on services pendant | 1 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | MSP | MMSP-091 | LIGHT HEAD: operating, articulated arm, pendant mounted | 1 | 1 | Pendant 3 - Arm 1
ENPR | Procedure Room - Endoscopy | MSP | MMOP-352 | PATCH PANEL: digital room operating (DOR) integration, on services pendant | 1 | 1 | Pendant 1
ENPR | Procedure Room - Endoscopy | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
ENPR | Procedure Room - Endoscopy | SER | ELGP-161 | GPO: single, UPS, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1
ENPR | Procedure Room - Endoscopy | SER | ELPR-011 | MONITOR: line isolation, wall mounted | 1 | 1 |  | to UPS power outlets on medical services pendants
ENPR | Procedure Room - Endoscopy | SER | ELSW-042 | SWITCH: light, laser in use | 1 | 1 |  | optional - to be provided if laser to be used, may be integrated on lighting control panel
ENPR | Procedure Room - Endoscopy | SER | ELSW-043 | SWITCH: light, x-ray in use | 1 | 1 |  | optional - to be provided if x-ray to be used, may be integrated on lighting control panel
ENPR | Procedure Room - Endoscopy | SER | ELSW-051 | CONTROL PANEL: lighting | 2 | 1
ENPR | Procedure Room - Endoscopy | SER | ITCL-081 | CONTROL PANEL: master clock system | 1 | 1
ENPR | Procedure Room - Endoscopy | SER | ITCL-181 | BUTTON: staff assist, with cancel, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | SER | ITCL-191 | BUTTON: emergency, with cancel, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to wall mounted telephone
ENPR | Procedure Room - Endoscopy | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 1
ENPR | Procedure Room - Endoscopy | SER | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 |  | optional - to drug safe if provided
ENPR | Procedure Room - Endoscopy | SER | LIFX-212 | LIGHT: illuminated sign, laser in use | 3 | 1 |  | located outside doors, optional - to be provided if laser to be used
ENPR | Procedure Room - Endoscopy | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 3 | 1 |  | located outside doors, optional - to be provided if x-ray to be used
ENPR | Procedure Room - Endoscopy | SER | MEEX-041 | GRILLE: exhaust, wall mounted, low level | 1 | 1 |  | for removal of anaesthetic gases, rectilinear or triangular ducts are also acceptable
ENPR | Procedure Room - Endoscopy | SER | MGFP-001 | ALARM: medical gases, panel, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | SER | MMOP-346 | CONTROL PANEL: operating lights, wall mounted | 1 | 1
ENPR | Procedure Room - Endoscopy | SER | MMOP-362 | OUTLET: digital operating room (DOR) integration, wall mounted | 1 | 1 |  | to wall mounted display screen
This shape represents a table slicer. Table slicers are not supported in this version of Excel.
If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## SC Set for Publish (hidden)
Code
1BR-IC
1BR-BA