## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
ENS-BR-A | Ensuite - Birthing Room | 10 |  | 1 patient; 1-2 staff assisting | 24 Hours | Sound attenuation level high, Acoustic privacy is required. | The Birthing Room Ensuite is for the Birthing Room patient to wash, shower, use the toilet, and bath as desired for pain relief, either independently or with assistance. The area and layout must accommodate an assisting nurse. The Ensuite will include a shower, handbasin, toilet and an island bath. The island bath will include steps and a seating platform at the bath edge. Acoustics: Sound attenuation level - High. Acoustic privacy required. Body Protected Electrical Area Additional Design Requirements: - The shower floor must not have a raised hob - The entrance is to be flush with the adjoining flooring - The door is to be fitted with escape hardware

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
ENS-BR-A | Ensuite - Birthing Room | FE | FE-2800 | Basin - handwash, Type B | 1 | refer to BHWS-B (sim) |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENS-BR-A | Ensuite - Birthing Room | FE | FE-3200 | Bath - patient | 1 | island, with steps & seating platform |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENS-BR-A | Ensuite - Birthing Room | FE | FE-47400 | Shower - hand-held | 1 |  |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENS-BR-A | Ensuite - Birthing Room | FE | FE-47400 | Shower - hand-held | 1 | low level over bath |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENS-BR-A | Ensuite - Birthing Room | FE | FE-55605 | Toilet suite - patient | 1 |  |  |  |  | No | No | Yes | No | Yes | No | Yes | No | No
ENS-BR-A | Ensuite - Birthing Room | FE | FE-40406 | Tapware - shower mixer | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | FF | FF-10800 | Hook - for IV flasks | 3 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | FF | FF-13700 | Mirror | 1 | over basin |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | FF | FF-16250 | Oxygen flowmeter | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | FF | FF-20650 | Soap / shampoo holder | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | FF | FF-2300 | Chair - shower | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | FF | FF-23700 | Towel rail | 1 | with grab rail strength and fixings |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | FF | FF-3400 | Coathook | 2 | 1 @ 1200 AFFL for wheelchair users |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | FF | FF-4800 | Curtain track - shower (90deg) | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | FF | FF-5300 | Curtain - shower | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | FF | FF-6152 | Dispenser - disposable glove | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | FF | FF-6154 | Dispenser - paper/ hand towel | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | FF | FF-6156 | Dispenser - soap | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | FF | FF-6160 | Dispenser - toilet paper | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | FF | FF-8400 | Grab rail - WC | 2 | 1 behind toilet, 1 to side |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | FF | FF-8430 | Grab rail - Bath | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | FF | FF-8450 | Grab rail - Shower | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | FF | FF-8500 | Grab rail - WC, hinged | 1 | optional, drop down rail |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | FF | FF-9200 | Hook - for catheter bag | 3 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | FF | FF-5824 | Waste bin - general | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | SE | S-9001 | GPO: Double | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | SE | S-9040 | Body protected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | SE | S-4000 | Hot water: outlet | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | SE | S-4010 | Cold water: outlet | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | SE | S-4033 | Floor waste | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | SE | S-5019 | Exhaust | 1 | for steam/ heat |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | SE | S-6001 | General: colour corrected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | SE | S-6200 | Light switches | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | SE | S-8000 | Patient/ Staff call | 3 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | SE | S-8010 | Staff/ Nurse assist call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | SE | S-8080 | Emergency call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | SE | S-1951 | Staff assist call | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | SE | S-2072 | Scavenge Outlet | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | SE | S-7000 | Oxygen (O2) | 1 | Optional |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | SE | S-7010 | Nitrous Oxide (N2O) | 1 | Optional |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | SE | S-7070 | Scavenge | 1 | Optional |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | SE | S-11000 | Wall panel | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | Fabrics | 1025 | Floor finish | 1 | Tiles also acceptable | Vinyl, non slip | Studded | Seamless, coved | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | Fabrics | 3070 | Wall finish | 1 | to wet areas; tiles also acceptable | Vinyl | Prefinished | Wall vinyl full height | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | Fabrics | 5023 | Ceiling - Plasterboard | 1 |  | Plasterboard | Prefinished | Water resistant, drop in tiles, 600x1200 | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | Fabrics | 8010 | Door protection | 1 | Equal to Acrovyn | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | Fabrics | 8040 | Door protection | 1 | Equal to Acrovyn | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | Fabrics | 9001 | Door - 1100mm | 1 | 910 clear outward opening, privacy latch, emergency release | Solid Core | Paint | Single leaf | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | Fabrics | 7001 | Windows | 1 | optional, obscure glass |  |  |  | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
ENS-BR-A | Ensuite - Birthing Room | Fabrics | 2000 | Skirting | 1 | or tiles for a tiled floor | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No