## Room Data
Standard Components - Room Data Sheet
Date of issue: 12.07.2023
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
ENS-BR | Ensuite - Birthing | 7 | 24 Hours | 1 mother; 1-2 staff assisting |  | Sound attenuation level high, Acoustic privacy is required. | An Ensuite - Birthing Room is for a mother to wash, shower and use the toilet, either independently or with assistance. During labour, the shower may be used for extended periods to manage pain and two shower heads are provided to support this. The area and layout must accommodate an assisting midwife and a support person. Additional Considerations: The Ensuite - Birthing will have direct access from the Birthing Room. The shower floor must not have a raised hob and the entrance to the ensuite is to be flush with the adjoining flooring. A ladder or other wall mounted supportive fixtures may be included to provide support at various heights and facilitate different postures during active birthing. A birthing woman's entire weight may be supported on this item, therefore the strength of the item and fixings, including in-wall support, to be equivalent to heavy duty grab rails. Item to be suitable for wet area.

## Items
Standard Components - Items in room
Date of issue: 12.07.2023
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
ENS-BR | Ensuite - Birthing | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | to be tiles for a tiled floor
ENS-BR | Ensuite - Birthing | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | to be suitable for bare feet; tiles are also acceptable
ENS-BR | Ensuite - Birthing | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
ENS-BR | Ensuite - Birthing | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | tiles are also acceptable
ENS-BR | Ensuite - Birthing | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1 | water resistant ceiling tiles are also acceptable
ENS-BR | Ensuite - Birthing | FA | DWSC-011 | DOOR: 1100mm c/o, single leaf, solid core, paint | 1 | outward opening, with privacy latch and emergency release
ENS-BR | Ensuite - Birthing | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
ENS-BR | Ensuite - Birthing | FFE | FIHR-026 | HOOK: coat | 2 | optional
ENS-BR | Ensuite - Birthing | FFE | FIRT-034 | TRACK: curtain, shower, 90 deg | 1 | optional, dependent on project/service requirements
ENS-BR | Ensuite - Birthing | FFE | FQGE-011 | CURTAIN: shower | 1 | optional, dependent on project/service requirements
ENS-BR | Ensuite - Birthing | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
ENS-BR | Ensuite - Birthing | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1
ENS-BR | Ensuite - Birthing | FFE | FIDI-030 | DISPENSER: soap | 1
ENS-BR | Ensuite - Birthing | FFE | FIDI-036 | DISPENSER: toilet paper | 1
ENS-BR | Ensuite - Birthing | FFE | FIRT-006 | GRAB RAIL: WC | 1
ENS-BR | Ensuite - Birthing | FFE | FIRT-003 | GRAB RAIL: shower, horizontal | 2
ENS-BR | Ensuite - Birthing | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | over basin
ENS-BR | Ensuite - Birthing | FFE | MGFP-004 | FLOWMETER: oxygen | 1
ENS-BR | Ensuite - Birthing | FFE | FQCW-037 | BIN: waste, sanitary | 1
ENS-BR | Ensuite - Birthing | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1
ENS-BR | Ensuite - Birthing | FFE | FIRT-016 | RAIL: towel | 1 | strength and fixings, including in-wall support, to be equivalent to grab rails
ENS-BR | Ensuite - Birthing | FFE | HYWC-001 | TOILET SUITE: accessible | 1 | accessible suite to assist with mobility and support during labor
ENS-BR | Ensuite - Birthing | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1
ENS-BR | Ensuite - Birthing | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 2
ENS-BR | Ensuite - Birthing | FFE | HYTP-020 | SHOWER: hand-held | 2
ENS-BR | Ensuite - Birthing | FFE | HYBA-002 | BASIN: ensuite, with vanity unit | 1
ENS-BR | Ensuite - Birthing | FFE | FIGE-011 | BACKREST: accessible toilet | 1
ENS-BR | Ensuite - Birthing | FFE | MMMA-019 | SUPPORT FIXTURE: birthing, ladder, wall mounted, wet area | 1 | optional; strength and fixings, including in-wall support, to be equivalent to heavy duty grab rails
ENS-BR | Ensuite - Birthing | SE | ITCL-008 | BUTTON: nurse call, staff assist | 2 | with indicator button and light, IPX4 rating required
ENS-BR | Ensuite - Birthing | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1
ENS-BR | Ensuite - Birthing | SE | HYDR-004 | DRAIN: floor waste | 2
ENS-BR | Ensuite - Birthing | SE | ELBO-015 | SWITCH: light, single | 1 | IPX4 rating required, located outside room
ENS-BR | Ensuite - Birthing | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
ENS-BR | Ensuite - Birthing | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1
ENS-BR | Ensuite - Birthing | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | with indicator button and light, IPX4 rating required
ENS-BR | Ensuite - Birthing | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | with indicator button and light, IPX4 rating required
ENS-BR | Ensuite - Birthing | SE | ELGP-208 | GPO: double, wall mounted | 1 | to be classified as a shaver outlet
ENS-BR | Ensuite - Birthing | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1