## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
ENS-BR | Ensuite - Birthing | Maternity | Translation and QA Only | 7 | 2400 |  | 2 | 07.04.2026 |  | 24 hours | 1 mother;; 1-2 staff / support persons assisting | An Ensuite - Birthing Room is for a mother to wash, shower and use the toilet, either independently or with assistance. During labour, the shower may be used for extended periods to manage pain and two shower heads are provided to support this. | ~ The area and layout must accommodate an assisting midwife and a support person. ~ The Ensuite - Birthing will have direct access from the Birthing Room. ~ The shower floor must not have a raised hob and the entrance to the ensuite is to be flush with the adjoining flooring. ~ A ladder or other wall mounted supportive fixtures may be included to provide support at various heights and facilitate different postures during active birthing. A birthing woman's entire weight may be supported on this item, therefore the strength of the item and fixings, including in-wall support, to be equivalent to heavy duty grab rails. Item to be suitable for wet area. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
ENS-BR | Ensuite - Birthing | Maternity | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | DWPR-005] to ensuite side
ENS-BR | Ensuite - Birthing | Maternity | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | DWPR-005] to birthing room side
ENS-BR | Ensuite - Birthing | Maternity | D+W | DOHI-007.01 | DOOR: hinged, 1 leaf, 1100 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-011] outward opening, with privacy latch and emergency release
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIBM-102 | MIRROR: fixed, safety glass, frameless | 1 | 1 |  | [FIBM-006] over basin
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025]
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030]
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIDI-281 | HOLDER: soap/shampoo, wall mounted | 1 | 1 |  | [FIDI-049]
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIDI-301 | DISPENSER: toilet paper, wall mounted | 1 | 1 |  | [FIDI-036]
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 3 |  | [FIHR-026] optional
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIRT-061 | TRACK: curtain, shower | 1 | 3 |  | [FIRT-034] optional, dependent on project/service requirements
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIRT-125 | GRAB RAIL: toilet, 90 degree | 1 | 1 |  | [FIRT-006]
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIRT-151 | GRAB RAIL: shower, straight, horizontal | 2 | 1 |  | [FIRT-003]
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIRT-191 | BACK REST: toilet, accessible | 1 | 1 |  | [FIGE-011]
ENS-BR | Ensuite - Birthing | Maternity | FFE | FIRT-206 | RAIL: towel, wall mounted | 1 | 1 |  | [FIRT-016] strength and fixings, including in-wall support, to be equivalent to grab rails
ENS-BR | Ensuite - Birthing | Maternity | FFE | FQGE-102 | CURTAIN: shower | 1 | 3 |  | [FQGE-011] optional, provision to be confirmed to suit local IPC policies and operational models for cleaning/replacement of curtains
ENS-BR | Ensuite - Birthing | Maternity | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
ENS-BR | Ensuite - Birthing | Maternity | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1 |  | [FQCW-037]
ENS-BR | Ensuite - Birthing | Maternity | FFE | HYBA-143 | BASIN: type C, handwashing, with integral double shelf | 1 | 1 |  | [HYBA-002]
ENS-BR | Ensuite - Birthing | Maternity | FFE | HYSH-056 | SHOWER: hand-held, connection on wall, bracket on vertical wall mounted rail | 2 | 1 |  | [HYTP-020]
ENS-BR | Ensuite - Birthing | Maternity | FFE | HYTP-051 | TAPWARE: basin, mixer, fixture mounted | 1 | 1 |  | [HYTP-036] selection of basin and tapware to be coordinated to ensure compatibility
ENS-BR | Ensuite - Birthing | Maternity | FFE | HYTP-251 | TAPWARE: shower, mixer | 2 | 1 |  | [HYTP-039]
ENS-BR | Ensuite - Birthing | Maternity | FFE | HYWC-033 | TOILET SUITE: patient, accessible | 1 | 1 |  | [HYWC-001] accessible suite to assist with mobility and support during labor
ENS-BR | Ensuite - Birthing | Maternity | FFE | MMMA-117 | SUPPORT FIXTURE: birthing, ladder, wall mounted, wet area | 1 | 3 |  | [MMMA-019] optional; strength and fixings, including in-wall support, to be equivalent to heavy duty grab rails
ENS-BR | Ensuite - Birthing | Maternity | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
ENS-BR | Ensuite - Birthing | Maternity | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-009]
ENS-BR | Ensuite - Birthing | Maternity | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009] moisture resistant drop-in ceiling tiles are also acceptable
ENS-BR | Ensuite - Birthing | Maternity | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
ENS-BR | Ensuite - Birthing | Maternity | FIN | FLVY-113 | FLOOR FINISH: vinyl, seamless, non-slip, wet area | 1 | 1 | Floor Finish 1 | [FLVY-009] to be suitable for bare feet; tiles are also acceptable
ENS-BR | Ensuite - Birthing | Maternity | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1 | [WLWA-019] tiles are also acceptable
ENS-BR | Ensuite - Birthing | Maternity | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 1 | Panel 1 | [MGAS-032]
ENS-BR | Ensuite - Birthing | Maternity | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042]
ENS-BR | Ensuite - Birthing | Maternity | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 1 | Panel 1 | [MGAS-053]
ENS-BR | Ensuite - Birthing | Maternity | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004]
ENS-BR | Ensuite - Birthing | Maternity | MSP | MGFP-051 | ADAPTER: scavenge | 1 | 1 | Panel 1 | [MMGE-001]
ENS-BR | Ensuite - Birthing | Maternity | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
ENS-BR | Ensuite - Birthing | Maternity | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 1 | 1 |  | [ELGP-208] to be classified as a shaver outlet
ENS-BR | Ensuite - Birthing | Maternity | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015] located outside room
ENS-BR | Ensuite - Birthing | Maternity | SER | HYDR-021 | DRAIN: floor waste, round | 2 | 1 |  | [HYDR-004]
ENS-BR | Ensuite - Birthing | Maternity | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
ENS-BR | Ensuite - Birthing | Maternity | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 3 | 1 |  | 1 to basin tapware, 2 to showers
ENS-BR | Ensuite - Birthing | Maternity | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 3 | 1 |  | 1 to basin tapware, 2 to showers
ENS-BR | Ensuite - Birthing | Maternity | SER | ITCL-122 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted, wet area | 2 | 1 |  | [ITCL-006] with indicator button and light, IPX4 rating required
ENS-BR | Ensuite - Birthing | Maternity | SER | ITCL-182 | BUTTON: nurse call, staff assist, with cancel, wall mounted, wet area | 1 | 1 |  | [ITCL-008] with indicator button and light, IPX4 rating required
ENS-BR | Ensuite - Birthing | Maternity | SER | ITCL-192 | BUTTON: nurse call, emergency, with cancel, wall mounted, wet area | 1 | 1 |  | [ITCL-004] with indicator button and light, IPX4 rating required