## Room Template Data
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Website - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | Full AHIA Review | 5 | 2700 | ENS-MH-A | 6 | 31.03.2026 | https://healthfacilityguidelines.com.au/component/ensuite-mental-health-inboard/?fullscreen=true&utm_source=project-link&rev=6 | 24 hours | 1 patient;; 1 staff assisting as required | The Ensuite - Mental Health, Inboard provides a shower, toilet and basin for use by consumers in a mental health inpatient unit. The inboard ensuite layout is used in conjunction with the 1 Bed Room - Mental Health, Inboard Ensuite (1BR-MH-IN). | ~ Unique requirements will exist in different care settings (i.e. intensive care, high dependency, acute, sub-acute, non-acute, units for children and adolescents, unit for older persons, etc.) and confirmation of the factors to be considered to meet the different service requirements and patient cohorts is required at project level. ~ All fittings and fixtures used must be of a type manufactured and marketed as anti-ligature. Requirements for the selection of suitable finishes, hardware, fixtures and fittings (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. ~ Where an accessible room is required to be provided, in order for the room to meet accessibility requirements, anti-ligature fittings may require a performance solution. This must be considered and addressed at project level with appropriate accessibility and building code consultants to meet applicable legislation and standards. ~If provided, all glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, sub-acute, acute, high dependency, intensive care, etc.). ~ The ceiling height is indicated as 2.7m. Based on a risk assessment, the ceiling height is to be confirmed at a project level. Selection of FF&E is to be considered in conjunction with assessing ceiling height to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. A plywood backing to the ceiling finish may be considered to provide a robust, impact resistance surface, particularly in high dependency and intensive care areas. ~ The ensuite door configuration is to be confirmed at project level to suit service requirements and jurisdictional policies. The door in this Standard Component is indicated as a solid door with an angled cut down at top and optional undercut at bottom. Alternatively, magnetic load release leaf/saloon style doors may be provided. Anti-ligature sliding doors may also be considered based on a risk assessment and review of available products. Configuring the bedroom and ensuite arrangement to provide privacy without a door may be considered, however patient privacy and dignity and overall bedroom observation in this type of layout should be carefully assessed with users. It is recommended that the door set is selected as a full assembly to ensure the leaf, frame and hardware are coordinated and meet all tamper proof, anti-ligature and anti-barricade requirements when used together. It is recommended that projects review in-situ installations/prototypes to confirm which solution addresses all requirements of their mental health environment. ~ The inclusion of door top or top and side anti-ligature alarms connected to the emergency call/duress systems may be assessed at project level to suit service requirements. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. The location of Wi-Fi access points is to be carefully considered to ensure strong coverage is provided for mobile duress functions. ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere. Interior design should aim to eliminate an institutional feel. Flooring, skirting and wall finish selections are to be considered at project level based on risk assessment for provision of alternative options (e.g. tiles). ~ Where caulking is required for finishing between surfaces it is recommended "anti-pick" caulking is used. ~ Coat hooks are shown as optional. Some jurisdictions do not support the provision of coat hooks of any type (e.g. Victoria), refer to jurisdictional policies for guidance. In areas where coat hooks have been excluded, provision of shelf space for the placement of dry towels/clothing is to be considered. ~ Provision of motion sensor lighting or switched lighting is to be considered and confirmed at project level. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE

## Items In Room Template
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 31
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | D+W | DOHI-003.03 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature | 1 | 1 | Internal - Door 1 | with angled cut down from top; may alternatively be provided as magnetic leaf/saloon style doors
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | located outside room
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIBM-152 | MIRROR: fixed, safety glass, toughened and laminated, frameless, tamper proof, anti-ligature | 1 | 1 |  | material to be confirmed at project level to suit service requirements
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIDI-257 | DISPENSER: soap, wall mounted, tamper proof, anti-ligature | 1 | 1 |  | to basin
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIDI-283 | HOLDER: soap/shampoo, wall recessed, tamper proof, anti-ligature | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIDI-302 | DISPENSER: toilet paper, wall mounted, tamper proof, anti-ligature | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIHR-027 | HOOK: coat, collapsible, tamper proof, anti-ligature, wall mounted | 2 | 1 |  | optional; some jurisdictions do not support the provision of coat hooks (e.g. Victoria), refer to jurisdictional policies for guidance; in areas where coat hooks have been excluded, provision of shelf space for the placement of dry towels/clothing is to be considered
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIRT-066 | TRACK: curtain, shower, collapsible/load release, tamper proof, anti-ligature | 1 | 1 |  | optional
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIRT-124 | GRAB RAIL: toilet, straight, vertical, tamper proof, anti-ligature | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FIRT-154 | GRAB RAIL: shower, straight, vertical, tamper proof, anti-ligature | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FIN | FLSK-022 | SKIRTING: vinyl, integral with floor vinyl, coved, tamper proof, anti-ligature | 6 | 1 | Floor Skirting | to be tiles if tiled floor provided
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FIN | FLVY-114 | FLOOR FINISH: vinyl, seamless, non-slip, wet area, barefoot | 1 | 1 | Floor Finish 1 | based on a risk assessment tiles may also be acceptable
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FQGE-104 | CURTAIN: shower, with load release runners | 1 | 3 |  | optional
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | FQWS-331 | BIN: sanitary waste | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | HYBA-152 | BASIN: type C, handwashing, tamper proof, anti-ligature, with integral single shelf | 1 | 1 |  | location of thermostatic mixing valve to be determined based on need to restrict consumer access and ability to share with nearby fittings
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | HYDR-022 | DRAIN: floor waste, round, tamper proof, anti-ligature, tamper proof | 2 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | HYDR-082 | DRAIN: clear out, round, tamper proof, anti-ligature, tamper proof | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | HYSH-006 | SHOWER: fixed rose, wall mounted, tamper proof, anti-ligature | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | HYTP-004 | FLUSH BUTTON: toilet suite, tamper proof, anti-ligature | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | HYTP-069 | TAPWARE: basin, tap set, wall mounted, tamper proof, anti-ligature | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | HYTP-263 | TAPWARE: shower, tap set, tamper proof, anti-ligature | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FFE | HYWC-036.02 | TOILET SUITE: patient, tamper proof, anti-ligature, concealed cistern | 1 | 1
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 1 |  | to toilet
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | SER | ITCL-122 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted, wet area | 1 | 1 |  | to shower
ENS-MH-IN | Ensuite - Mental Health, Inboard | Mental Health | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 7 | 1 | Wall Finish 1 | based on a risk assessment tiles may also be acceptable