## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Single line edit) | (Single line edit) | (Single line edit) | (Single line edit)
ENS-MH | Ensuite - Mental Health | 5 |  | 1 patient; 1 staff assisting as required | 24 Hours | Sound attenuation level high, Acoustic privacy is required. | The Ensuite - Mental Health will provide a shower, toilet and handbasin for use by mental health patients. The Ensuite will be lockable and Master Keyed from the outside with a privacy latch on the inside. The Ensuite - Mental Health may vary in configuration to suit different room types including: - ENS-MH-A Inboard Ensuite with direct access, for 1 or 2 Bed Rooms - ENS-MH-B Inboard Ensuite with access from corridor, for 1 or 2 Bed Rooms - ENS-MH-D Inboard Ensuite for 2 Bed Room, with direct access Acoustics: Sound attenuation level high; Acoustic privacy required Body Protected electrical area Additional Design Considerations: - Two floor wastes will be required - Fittings are to have a breaking strain of not more than 15 kg - Grab rails, shower and door furniture must not provide points for ligature - Cisterns should be concealed - All glazing in the room including mirror to be unbreakable - An 'observation bay' which may include thermostatic mixing & shut off valves and RCD is optional

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No)
ENS-MH | Ensuite - Mental Health | Fabrics | 1025 | Floor finish | 1 | tiles also acceptable | Vinyl, non slip | Studded | Seamless, coved | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | Fabrics | 2000 | Skirting | 1 | or tiles for a tiled floor | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | Fabrics | 3070 | Wall finish | 1 | to wet areas; tiles also acceptable | Vinyl | Prefinished | Wall vinyl full height | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | Fabrics | 5021 | Ceiling - Plasterboard | 1 |  | Plasterboard | Paint, washable | Water resistant, flush set, suspended | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | Fabrics | 6010 | Cornice | 1 |  | Plasterboard | Paint | 90mm to match ceiling finish | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | Fabrics | 8010 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | Fabrics | 8040 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | Fabrics | 9001 | Door - 1100mm | 1 | 910 clear outward opening, privacy latch; anti-hang door hardware | Solid Core | Paint | Single leaf | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | FE | FE-1142 | Toilet suite - concealed cistern | 1 | accessible height for patient use |  |  |  | No | No | Yes | No | Yes | No | Yes | No | No
ENS-MH | Ensuite - Mental Health | FE | FE-2850 | Basin - handwash, Type C (with vanity) | 1 | taps and spout with no ligature points |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENS-MH | Ensuite - Mental Health | FE | FE-40412 | TAP - COLD | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | FE | FE-40413 | TAP - HOT | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | FE | FE-47550 | Shower - corrective services | 1 | tapware with no ligature points |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENS-MH | Ensuite - Mental Health | FF | FF-1327 | Grab rail with infill - Shower | 1 | vertical |  |  |  | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | FF | FF-1328 | Grab rail with infill - WC | 1 | vertical |  |  |  | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | FF | FF-1329 | Coathook - collapsible | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | FF | FF-1331 | Shelf - vanity, recessed | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | FF | FF-1332 | Curtain track - ceiling, recessed | 1 | plastic, collapsible curtain |  |  |  | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | FF | FF-13730 | Mirror - acrylic | 1 | or safety glass mirror |  |  |  | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | FF | FF-20603 | Soap / shampoo holder - recessed (h) | 1 | to shower |  |  |  | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | FF | FF-5300 | Curtain - shower | 1 | collapsible; anti-hang fabric |  |  |  | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | FF | FF-5824 | Waste bin - general | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | FF | FF-6154 | Dispenser - paper/ hand towel | 1 | plastic; no ligature points; no sharp cutting edges |  |  |  | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | FF | FF-6156 | Dispenser - soap | 1 | optional; no ligature points; no sharp cutting edges |  |  |  | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | FF | FF-6160 | Dispenser - toilet paper | 1 | no ligature points; no sharp cutting edges |  |  |  | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | SE | S-1086 | General fluorescent: vandal proof | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | SE | S-4033 | Floor waste | 2 | vandal proof |  |  |  | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | SE | S-5000 | Airconditioning | 1 | with vandal proof outlet |  |  |  | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | SE | S-5019 | Exhaust | 1 | for heat/ steam; with vandal proof outlet |  |  |  | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | SE | S-8000 | Patient/ Staff call | 2 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
ENS-MH | Ensuite - Mental Health | SE | S-9040 | Body protected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No