## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Single line edit) | (Single line edit) | (Single line edit) | (Single line edit)
ENS-SH | Ensuite - Shared | 6 |  | 1 patient; 1 staff assisting | 24 Hours | Sound attenuation level high, Acoustic privacy is required. | An Ensuite - Shared is for a patient to wash, shave, groom themselves, shower and use the toilet, either independently or with assistance. The area and layout must accommodate an assisting nurse, patient lifter and wheelchair access. The Ensuite shared may be accessed from two patient rooms. Special privacy latching will be required to lock both entry doors on activation. The actual choice of Ensuite will depend on the patient type and the Operational Policy of the facility. The Ensuite - Shared may vary in configuration to suit different patient types or room types including: - ENS-SH-A Shared ensuite - standard - ENS-SH-B Shared ensuite with additional access Acoustics: Sound attenuation level - High. Acoustic privacy required. Body Protected Electrical Area Additional Design Requirements: - The shower floor must not have a raised hob - The entrance is to be flush with the adjoining flooring

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No)
ENS-SH | Ensuite - Shared | Fabrics | 1025 | Floor finish | 1 | Tiles also acceptable | Vinyl, non slip | Studded | Seamless, coved | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | Fabrics | 2000 | Skirting | 1 | or tiles for a tiled floor | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | Fabrics | 3070 | Wall finish | 1 | to wet areas; tiles also acceptable | Vinyl | Prefinished | Wall vinyl full height | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | Fabrics | 5023 | Ceiling - Plasterboard | 1 |  | Plasterboard | Prefinished | Water resistant, drop in tiles, 600x1200 | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | Fabrics | 8010 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | Fabrics | 8040 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | Fabrics | 9001 | Door - 1100mm | 1 | 910 clear outward opening, privacy latch | Solid Core | Paint | Single leaf | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | FE | FE-40406 | Tapware - shower mixer | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | FE | FE-47400 | Shower - hand-held | 1 |  |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENS-SH | Ensuite - Shared | FE | FE-55605 | Toilet suite - patient | 1 |  |  |  |  | No | No | Yes | No | Yes | No | Yes | No | No
ENS-SH | Ensuite - Shared | FE | FE-5603 | Basin - ensuite | 1 |  |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENS-SH | Ensuite - Shared | FF | FF-13700 | Mirror | 1 | over basin |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | FF | FF-20650 | Soap / shampoo holder | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | FF | FF-2300 | Chair - shower | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | FF | FF-23700 | Towel rail | 2 | with grab rail strength and fixings |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | FF | FF-3400 | Coathook | 2 | 1 @ 1200 AFFL for wheelchair users |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | FF | FF-4800 | Curtain track - shower (90deg) | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | FF | FF-530 | Basin vanity top | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | FF | FF-5300 | Curtain - shower | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | FF | FF-5824 | Waste bin - general | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | FF | FF-6152 | Dispenser - disposable glove | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | FF | FF-6154 | Dispenser - paper/ hand towel | 1 | optional |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | FF | FF-6156 | Dispenser - soap | 1 | optional |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | FF | FF-6160 | Dispenser - toilet paper | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | FF | FF-8400 | Grab rail - WC | 1 | 1 to side |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | FF | FF-8450 | Grab rail - Shower | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | FF | FF-8500 | Grab rail - WC, hinged | 1 | drop down rail, optional for standard shared ensuite |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | FF | FF-8500 | Grab rail - WC, hinged | 1 | to both sides of WC in additional access ensuite |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | SE | S-1951 | Staff assist call | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | SE | S-4033 | Floor waste | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | SE | S-5019 | Exhaust | 1 | for heat/ steam |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | SE | S-6000 | General fluorescent | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | SE | S-6200 | Light switches | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | SE | S-8000 | Patient/ Staff call | 2 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | SE | S-8010 | Staff/ Nurse assist call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | SE | S-8080 | Emergency call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | SE | S-9001 | GPO: Double | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared | SE | S-9040 | Body protected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No