## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Single line edit) | (Single line edit) | (Single line edit) | (Single line edit)
ENS-ST | Ensuite - Standard | 5 |  | 1 patient; 1 staff assisting | 24 Hours | Sound attenuation level high, Acoustic privacy is required. | An Ensuite is for a patient to wash, shave, groom themselves, shower and use the toilet, either independently or with assistance. The area and layout must accommodate an assisting nurse and a shower commode. The Ensuite and Bedroom should be planned as an integrated suite so the layout is optimised across the two rooms. Acoustics: Sound attenuation level - High. Acoustic privacy required. Body Protected Electrical Area Additional Design Requirements: - The shower floor must not have a raised hob - The entrance is to be flush with the adjoining flooring - The door is to be fitted with escape hardware

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No)
ENS-ST | Ensuite - Standard | Fabrics | 2000 | Skirting | 1 | or tiles for a tiled floor | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | Fabrics | 2526 | Floor finish | 1 | Suitable for barefeet. Tiles also acceptable. | Vinyl | Non-slip | Seamless coved | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | Fabrics | 2529 | Door protection | 1 |  | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | Fabrics | 2530 | Door protection | 1 |  | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | Fabrics | 3070 | Wall finish | 1 | to wet areas; tiles also acceptable | Vinyl | Prefinished | Wall vinyl full height | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | Fabrics | 5023 | Ceiling - Plasterboard | 1 | water resistant flush set plasterboard ceiling also acceptable | Plasterboard | Prefinished | Water resistant, drop in tiles, 600x1200 | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | Fabrics | 9001 | Door - 1100mm | 1 | 910 clear outward opening, privacy latch, emergency release | Solid Core | Paint | Single leaf | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | FE | FE-40406 | Tapware - shower mixer | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | FE | FE-47400 | Shower - hand-held | 1 | Tapware: mixer, wall mounted, shower. |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENS-ST | Ensuite - Standard | FE | FE-55605 | Toilet suite - patient | 1 | With backrest. Concealed cistern, optional. |  |  |  | No | No | Yes | No | Yes | No | Yes | No | No
ENS-ST | Ensuite - Standard | FE | FE-5603 | Basin - ensuite | 1 | With integral shelf for patient belongings or separate shelf. Tapware: mixer, fixture mounted. |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENS-ST | Ensuite - Standard | FF | FF-13700 | Mirror | 1 | over basin |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | FF | FF-19100 | Waste bin - sanitary | 0 | Optional, depends on Waste Management Policy. |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | FF | FF-20650 | Soap / shampoo holder | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | FF | FF-2300 | Chair - shower | 1 | Or commode chair or combined shower/commode chair. |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | FF | FF-23700 | Towel rail | 1 | With grab rail strength and fixings to support bariatric capacity. |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | FF | FF-3400 | Coathook | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | FF | FF-4800 | Curtain track - shower (90deg) | 1 | Optional, depends on Infection Control Policy |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | FF | FF-5300 | Curtain - shower | 1 | Optional, depends on Infection Control Policy |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | FF | FF-5824 | Waste bin - general | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | FF | FF-6154 | Dispenser - paper/ hand towel | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | FF | FF-6156 | Dispenser - soap | 2 | 1 x basin. 1 x shower (optional). |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | FF | FF-6160 | Dispenser - toilet paper | 1 | Locate on drop down rail. |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | FF | FF-8400 | Grab rail - WC | 1 | 1 to side or wrap-around. |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | FF | FF-8450 | Grab rail - Shower | 1 | Combined with hand held shower. |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | FF | FF-8500 | Grab rail - WC, hinged | 1 | Drop down rails on both sides of WC; 1 x toilet paper dispenser, 1 x patient staff call 1 x NC. Fixings to support bariatric capacity. |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | FF | FF-8510 | Grab Rail - SS | 1 | behind toilet |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | SE | S-1951 | Staff assist call | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | SE | S-1983 | General fluoresecent downlights | 1 | Over toilet. |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | SE | S-4033 | Floor waste | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | SE | S-5015 | Ventilation | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | SE | S-5019 | Exhaust | 1 | for steam/ heat |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | SE | S-6000 | General fluorescent | 1 | Sensor light optional. |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | SE | S-8000 | Patient/ Staff call | 2 | + indicator button & light. |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | SE | S-8080 | Emergency call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | SE | S-9001 | GPO: Double | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
ENS-ST | Ensuite - Standard | SE | S-9040 | Body protected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No