## Room Template Data
Exit Bay (EXIT) - Room Template Properties and Room Template Data
2026-08-05
No. of Standard Components = 1
Code | Template Name | Standard Area | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Briefing - Hours of Operation - Duration - Duration | Briefing - Hours of Operation - Duration - extended/limited hours | Briefing - Hours of Operation - Hours/days - Open time | Briefing - Hours of Operation - Hours/days - Close time | Briefing - Hours of Operation - Hours/days - Days | Briefing - Hours of Operation - Comment | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experiance system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statuatory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magentic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: sensitive | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
EXIT | Exit Bay | 11 |  | 1 | 06.05.2025 | Up to 24 hours | 0 |  |  |  |  | staff intermittently | The Exit Bay provides area for patients and equipment to be moved from the Operating Room at the conclusion of a procedure. The Exit Bay provides space for the temporary storage of a patient bed while a procedure is in progress. Direct access to the Operating Room is required. | ~ Automated doors with motion or elbow activation are provided to the Operating Room from the Exit Bay. Buttons/sensors should be appropriately located in relation to the door, including consideration for approach and movement of patients on beds and mobile equipment. 2-gang buttons that support the opening of either one or both leaves of the door as required are desirable. ~ A cupboard for digital operating room (DOR) ICT/AV equipment is indicated on the layout but is not included in the overall area measurement and the contents of the ICT/AV cupboard are not captured in this Standard Component. The size of the ICT/AV cupboard will vary depending on equipment to be accommodated. Rather than being located individually to each Operating Room, ICT/AV equipment may be consolidated in a room that is shared between a number of Operating Rooms as appropriate to suit equipment installation, testing and maintenance requirements. ~ Medical gas valve boxes for each Operating Room are typically located in the associated Exit Bay. Size and location of the medical gas valve box zone, to be kept clear of all other services, is to be confirmed by a medical gas engineering consultant. ~ Height and type of wall finish to suit local infection prevention and control policies and rigorous cleaning regimes. Provision and height of corner guards as required to provide protection from anticipated mobile equipment movement. ~ Depending on the use of x-ray equipment within the adjacent Operating Room, radiation shielding may be required to this room and is to be assessed by a Radiation Consultant. | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE
This shape represents a table slicer. Table slicers are not supported in this version of Excel.
If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Items In Room Template
Standard Components - Items in Room Template
2026-08-05
No. of Standard Components = 1
Code | Template Name | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
EXIT | Exit Bay | D+W | AHDEC-036 | SWITCH: door release, double gang, automatic door, wall mounted | 1 | 1 | Internal - Door 1 | to allow for opening either one or both leaves of the door
EXIT | Exit Bay | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2
EXIT | Exit Bay | D+W | AFDPR-006.05 | DOOR PROTECTION: plate, full height | 1 | 1 | Internal - Door 1 | to both sides of door
EXIT | Exit Bay | D+W | DOHI-001.01 | DOOR: hinged, 1 leaf, 800 clear opening, solid | 1 | 1 | Internal - Door 2 | to ICT/AV cupboard
EXIT | Exit Bay | D+W | DOHI-212.03 | DOOR: hinged, 2 leaves, 1600 clear opening, solid, standard vision panel, with cover | 1 | 1 | Internal - Door 1 | to operating room (see OR-GEN)
EXIT | Exit Bay | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
EXIT | Exit Bay | FFE | FIHR-030 | HOOK: equipment, patient slide | 1 | 1
EXIT | Exit Bay | FFE | FIHR-171 | BRACKET: gas cylinder, single, wall mounted | 1 | 1 |  | clear space above the bracket for loading/unloading of the cylinder
EXIT | Exit Bay | FFE | MMBE-031 | SLIDE: patient transfer | 1 | 1
EXIT | Exit Bay | FFE | MGGE-011.01 | CYLINDER: medical gas, C size, oxygen | 1 | 1
EXIT | Exit Bay | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice
EXIT | Exit Bay | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1
EXIT | Exit Bay | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
EXIT | Exit Bay | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
EXIT | Exit Bay | FIN | WLFI-011.07 | WALL FINISH: vinyl, full height | 1 | 1 | Wall Finish 1
EXIT | Exit Bay | FIN | WLPR-006.07 | WALL PROTECTION: corner guards, full height | 1 | 1 | Wall Finish 2
EXIT | Exit Bay | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1
EXIT | Exit Bay | SER | MGFP-011 | VALVE BOX: medical gases | 1 | 1
This shape represents a table slicer. Table slicers are not supported in this version of Excel.
If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## SC Set for Publish (hidden)
Code
Operating | ANAES
Operating | B-SCRUB
Operating | CLNUP
Operating | ENPR
Operating | EXIT
Operating | OR-GEN
Operating | STSS