## Room Template Data
Fluoroscopy Control Room (FLUO-CTRL) - Room Template Properties and Room Template Data
2025-05-15
No. of Standard Components = 1
Code | Template Name | Standard Area | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Briefing - Hours of Operation - Duration - Duration | Briefing - Hours of Operation - Duration - extended/limited hours | Briefing - Hours of Operation - Hours/days - Open time | Briefing - Hours of Operation - Hours/days - Close time | Briefing - Hours of Operation - Hours/days - Days | Briefing - Hours of Operation - Comment | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experiance system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statuatory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magentic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: sensitive | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
FLUO-CTRL | Fluoroscopy Control Room | 13 | FLUOC | 2 | 15.05.2025 | Up to 24 hours | FALSE |  |  |  |  | up to 2 staff | The Fluoroscopy Control Room provides the space and equipment for remote control of fluoroscopy equipment and amenities for the review of images and reporting. Direct visibility of the patient through an observation window and direct access to the imaging room is required. | ~ Cable ducts for services between the imaging device and the control area will be required and must be coordinated with the MME vendor. Additional building services connections and outlets are to be coordinated to suit equipment requirements. ~ Radiation shielding requirements are to be assessed and advised by a qualified Radiation Consultant to suit the practice, workload and equipment procured, and all shielding on the Standard Component is indicative. ~ An ‘X-ray in Use’ light system is required with signs that are illuminated when the imaging device is on and turned off when it stops. Signs are to be at all doors entering the room. ~ The size, quantity and configuration of computer display screens is to be finalised based on the specific image display and processing task requirements (e.g. number of application windows to be viewed concurrently) and ergonomic considerations. Providing flexibility of monitor positioning is vital to ensure adjustments are possible to meet the ergonomic requirements of different users. ~ Provision of height adjustable workstations or fixed joinery is to be in line with service requirements and local WHS policies. ~ Hours of operation depend on the service in which this room is located. Ambulatory medical imaging services may only operate during business hours or extended business hours, some small hospital services may have an on-call, after-hours service. Large units are likely to provide a 24-hour service, especially where a satellite service is provided with an emergency department. ~ Requirement for fixed and/or mobile duress to be confirmed to suit service requirements. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ Provision of an intercom for staff communication within the department is dependent on service requirements. This function may be provided as part of the telephone system. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements and confirmed based on risk assessment considering the impact of a power outage on patient care/safety. | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Items In Room Template
Standard Components - Items in Room Template
2025-05-15
No. of Standard Components = 1
Code | Template Name | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
FLUO-CTRL | Fluoroscopy Control Room | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | Internal - Window 1
FLUO-CTRL | Fluoroscopy Control Room | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to control room side
FLUO-CTRL | Fluoroscopy Control Room | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | to control room side
FLUO-CTRL | Fluoroscopy Control Room | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to imaging room side
FLUO-CTRL | Fluoroscopy Control Room | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to corridor side, extent dependent on movement of beds and mobile equipment
FLUO-CTRL | Fluoroscopy Control Room | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 2 | optional - staff entry from corridor
FLUO-CTRL | Fluoroscopy Control Room | D+W | DOHI-013.05 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded, standard vision panel, lead glass | 1 | 1 | Internal - Door 1 | to imaging room
FLUO-CTRL | Fluoroscopy Control Room | D+W | WIFX-008.03 | WINDOW: fixed, internal, single glazed, sill at 1050H, shielded, lead glass | 1 | 1 | Internal - Window 1 | for observation from control room
FLUO-CTRL | Fluoroscopy Control Room | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | FFE | FIHR-126 | RACK: lead apron, multi, wall mounted | 1 | 1 |  | with in wall structural support to product specifications
FLUO-CTRL | Fluoroscopy Control Room | FFE | FIHR-201 | BRACKET: central processing unit (CPU), under bench/desk | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | FFE | FIHR-221 | BRACKET: computer display screen, dual, articulated, bench/desk mounted | 1 | 1 |  | to display/processing workstation
FLUO-CTRL | Fluoroscopy Control Room | FFE | FIHR-408 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | to slave patient monitor
FLUO-CTRL | Fluoroscopy Control Room | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 2 | 1
FLUO-CTRL | Fluoroscopy Control Room | FFE | FQSM-287 | CABINET: mobile, 1800H nominal, tambour unit | 1 | 1 |  | type and extent of storage to suit service requirements
FLUO-CTRL | Fluoroscopy Control Room | FFE | ITAV-146 | MICROPHONE: AV system, surface mounted, gooseneck | 1 | 1 |  | for communication with patient, may be integral to control unit provided by MME vendor
FLUO-CTRL | Fluoroscopy Control Room | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | FFE | ITNE-153 | COMPUTER: central processing unit (CPU), PACS | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | FFE | ITNE-172 | DISPLAY SCREEN: computer, PACS | 2 | 1 |  | display/processing workstation, on dual arm bracket
FLUO-CTRL | Fluoroscopy Control Room | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1 |  | bench height to be confirmed; adjustable height desks may be considered depending on WHS policies and coordination with services and observation window
FLUO-CTRL | Fluoroscopy Control Room | FFE | JOBE-211 | BENCH SUPPORT: bracket | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | FFE | JOBE-221 | BENCH SUPPORT: end panel | 1 | 1 |  | leg support is also acceptable
FLUO-CTRL | Fluoroscopy Control Room | FFE | JOBE-251 | CAP: cable access | 2 | 1
FLUO-CTRL | Fluoroscopy Control Room | FFE | MIFL-011 | CONTROL CONSOLE: fluoroscopy/screening, dual display screens, keyboard and mouse, control unit, desktop | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | FFE | MIFL-016 | COMPUTER: fluoroscopy/screening, central processing unit (CPU) | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | FFE | MIGE-041 | WARMER: contrast, benchtop | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | FFE | MMPM-051 | MONITOR: patient, slave | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice
FLUO-CTRL | Fluoroscopy Control Room | FIN | CLTI-021 | CEILING: drop-in tiles, prefinished | 1 | 1 | Ceiling Finish 1
FLUO-CTRL | Fluoroscopy Control Room | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
FLUO-CTRL | Fluoroscopy Control Room | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
FLUO-CTRL | Fluoroscopy Control Room | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
FLUO-CTRL | Fluoroscopy Control Room | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | SER | ELGP-161 | GPO: single, UPS, wall mounted | 1 | 1 |  | to slave patient monitor
FLUO-CTRL | Fluoroscopy Control Room | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | over desk for portable devices
FLUO-CTRL | Fluoroscopy Control Room | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | to contrast warmer
FLUO-CTRL | Fluoroscopy Control Room | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1
FLUO-CTRL | Fluoroscopy Control Room | SER | ELGP-261 | GPO: double, UPS, wall mounted | 2 | 1 |  | to control console, extent of UPS to be confirmed to suit service and equipment requirements
FLUO-CTRL | Fluoroscopy Control Room | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | SER | ELSW-021 | SWITCH: light, dimmer | 2 | 1 |  | to general room lighting, 1 to each door, 1 optional - to staff entry if provided
FLUO-CTRL | Fluoroscopy Control Room | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | main power emergency stop, refer to equipment manufacturer for safety and compatibility with equipment
FLUO-CTRL | Fluoroscopy Control Room | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | to slave patient monitor
FLUO-CTRL | Fluoroscopy Control Room | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 2 | 1
FLUO-CTRL | Fluoroscopy Control Room | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
FLUO-CTRL | Fluoroscopy Control Room | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | optional - inclusion dependent on service requirements and ICT policies, may be integral function of telephone, to control workstation area
FLUO-CTRL | Fluoroscopy Control Room | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 1 | 1 |  | to imaging room entry, to automatically turn on when modality is in use
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## SC Set for Publish (hidden)
Code
Administration | BMFD-3
Administration | BMFD-7
Administration | MEET-15
Administration | MEET-20
Administration | MEET-30
Administration | MEET-55
Administration | MEET-9
Administration | OFF-1P-12
Administration | OFF-1P-9
Administration | OFF-2P
Administration | OFF-WS
Administration | STFS-10
Administration | STFS-20
Allied Health | ADLB
Allied Health | ADLD
Allied Health | ADLK
Allied Health | ADLL
Allied Health | AUD-CR
Allied Health | AUD-TR
Allied Health | GYAH-GP
Allied Health | GYAH-ID
Allied Health | HYDP
Allied Health | PLST
Allied Health | TRMT-HTS
Allied Health | TRMT-POD
Ambulatory Care | BHW
Ambulatory Care | BWC
Ambulatory Care | CONS
Ambulatory Care | CONS-UN
Ambulatory Care | INTV
Ambulatory Care | PBTR-MD
Ambulatory Care | PROC
Ambulatory Care | TRMT
Cardiac Care | 1BR-CCU
Cardiac Investigations | CLAB-EP
Cardiac Investigations | CLAB-I
Cardiac Investigations | CLCR-EP
Cardiac Investigations | CLCR-I
Cardiac Investigations | CLUP-7
Cardiac Investigations | ECHO-TOE
Cardiac Investigations | STRT
Clinical Support Set 1 - Medication Rooms and Stores | AHDR
Clinical Support Set 1 - Medication Rooms and Stores | BHWS-A
Clinical Support Set 1 - Medication Rooms and Stores | BHWS-B
Clinical Support Set 1 - Medication Rooms and Stores | CLN-10
Clinical Support Set 1 - Medication Rooms and Stores | CLN-MED-20
Clinical Support Set 1 - Medication Rooms and Stores | CLN-MED-S
Clinical Support Set 1 - Medication Rooms and Stores | MED-14
Clinical Support Set 1 - Medication Rooms and Stores | STEQ-14
Clinical Support Set 1 - Medication Rooms and Stores | STEQ-20
Clinical Support Set 1 - Medication Rooms and Stores | STGN
Clinical Support Set 2 - Corridor Bays, Staff Stations and Lounges | BMEQ
Clinical Support Set 2 - Corridor Bays, Staff Stations and Lounges | BRES
Clinical Support Set 2 - Corridor Bays, Staff Stations and Lounges | CORR
Clinical Support Set 2 - Corridor Bays, Staff Stations and Lounges | LNGE-10
Clinical Support Set 2 - Corridor Bays, Staff Stations and Lounges | LNGE-20
Clinical Support Set 2 - Corridor Bays, Staff Stations and Lounges | OFF-CLN
Clinical Support Set 2 - Corridor Bays, Staff Stations and Lounges | OFF-WI-5
Clinical Support Set 2 - Corridor Bays, Staff Stations and Lounges | SSTN-10
Clinical Support Set 2 - Corridor Bays, Staff Stations and Lounges | SSTN-14
Clinical Support Set 2 - Corridor Bays, Staff Stations and Lounges | SSTN-20
Clinical Support Set 3 - Dirty Utilities and Equipment Clean-up | DTUR-10
Clinical Support Set 3 - Dirty Utilities and Equipment Clean-up | DTUR-12
Clinical Support Set 3 - Dirty Utilities and Equipment Clean-up | DTUR-14
Clinical Support Set 3 - Dirty Utilities and Equipment Clean-up | DTUR-S
Clinical Support Set 3 - Dirty Utilities and Equipment Clean-up | ECL-10
Clinical Support Set 3 - Dirty Utilities and Equipment Clean-up | ECL-12
Clinical Support Set 3 - Dirty Utilities and Equipment Clean-up | ECL-14
Clinical Support Set 3 - Dirty Utilities and Equipment Clean-up | ECL-8
Emergency | CONS-ENT-OP
Emergency | PBAT
Emergency | PBTR-A
Emergency | PBTR-AS
Emergency | PBTR-FT
Emergency | PBTR-NA
Emergency | PBTR-R
Emergency | REC-E
Emergency | TRIAGE-1
Emergency | TRIAGE-2
Inpatient Accommodation | 1BR-BA
Inpatient Accommodation | 1BR-IS-N1
Inpatient Accommodation | 1BR-IS-N2
Inpatient Accommodation | 1BR-SP-A1
Inpatient Accommodation | 1BR-SP-A2
Inpatient Accommodation | 1BR-ST-A1
Inpatient Accommodation | 1BR-ST-A2
Inpatient Accommodation | 1BR-ST-A3
Inpatient Accommodation | 1BR-ST-B1
Inpatient Accommodation | 1BR-ST-B2
Inpatient Accommodation | 1BR-ST-B3
Inpatient Accommodation | 1BR-ST-D
Inpatient Accommodation | 2BR-ST-A1
Inpatient Accommodation | 2BR-ST-A2
Inpatient Accommodation | 2BR-ST-B
Inpatient Accommodation | 4BR-ST
Inpatient Accommodation | ANRM
Inpatient Accommodation | ENS-ACC
Inpatient Accommodation | ENS-BA
Inpatient Accommodation | ENS-SH
Inpatient Accommodation | ENS-SP
Inpatient Accommodation | ENS-ST-A1
Inpatient Accommodation | ENS-ST-A2
Inpatient Accommodation | ENS-ST-A3
Inpatient Accommodation | ENS-ST-B
Inpatient Accommodation | ENS-ST-C
Intensive Care | 1BR-IC
Intensive Care | PBIC
Logistics / Support Services | BBEV
Logistics / Support Services | BLIN
Logistics / Support Services | BMT
Logistics / Support Services | CLRM
Logistics / Support Services | COMM
Logistics / Support Services | DINR
Logistics / Support Services | DISP-10
Logistics / Support Services | DISP-15
Logistics / Support Services | PTRY
Logistics / Support Services | SECR
Logistics / Support Services | STBK
Logistics / Support Services | STCL
Maternity | BIRM-A
Maternity | BIRM-B
Maternity | ENS-BR
Medical Imaging | CTIR
Medical Imaging | CTIR-CTRL
Medical Imaging | FLUO
Medical Imaging | FLUO-CTRL
Medical Imaging | MAMMO
Medical Imaging | MRI
Medical Imaging | MRI-CTRL
Medical Imaging | OPG
Medical Imaging | REPR
Medical Imaging | REPW
Medical Imaging | ULTR
Medical Imaging | ULTR-PR
Medical Imaging | XRAY
Medical Imaging | XRAY-OPG
Mental Health | 1BR-MH-A
Mental Health | 1BR-MH-C
Mental Health | DINBEV-25
Mental Health | ENS-MH-A
Mental Health | ENS-MH-B
Mental Health | INTF-MH
Mental Health | LAUN-MH
Mental Health | SECL
Mental Health | STPP
Mental Health | WAIT-SEC
Mortuary and Autopsy | MOR-AU
Mortuary and Autopsy | MOR-BH
Mortuary and Autopsy | MOR-BR
Mortuary and Autopsy | MOR-VR
Mortuary and Autopsy | MOR-W
Neonatal Care | LAUN-PT
Neonatal Care | NBIC-HD
Neonatal Care | NBLD
Nuclear Medicine / PET | PET-CT
Nuclear Medicine / PET | SPECT-CT
Nuclear Medicine / PET | SPECT-CTCR
Nuclear Medicine / PET | UTRM
Operating | ANAES
Operating | B-SCRUB
Operating | CLNUP
Operating | ENPR
Operating | EXIT
Operating | OR-GEN
Operating | STSS
Oral Health | DEN-MLB
Oral Health | DENSR-1
Oral Health | DENSR-2
Pathology | AHBF
Pathology | BBLD
Pathology | BES
Pathology | BPATH
Pathology | BPTS
Pathology | PBSC
Perioperative | BBW
Perioperative | CHPT
Perioperative | CHPT-AC
Perioperative | PT-HOLD-A
Perioperative | PT-HOLD-B
Perioperative | PT-RS1
Pharmacy | PHA-CO
Pharmacy | PHA-DB
Pharmacy | PHA-DS
Pharmacy | PHA-PR
Pharmacy | PHA-RE
Pharmacy | STAD
Public Areas | AIRLE-12
Public Areas | AIRLE-6
Public Areas | BVM
Public Areas | BWTR
Public Areas | PAR
Public Areas | PLAY
Public Areas | RECP-10
Public Areas | RECP-15
Public Areas | RECP-20
Public Areas | WAIT-10
Public Areas | WAIT-20
Public Areas | WAIT-30
Public Areas | WAIT-S
Radiation Oncology | CTPR
Radiation Oncology | LINAC
Radiation Oncology | LINAC-CR
Renal Dialysis | PBTR-RD-A
Renal Dialysis | PBTR-RD-B
Renal Dialysis | PLNT-WT
Sanitary Facilities | BATH
Sanitary Facilities | SHAC
Sanitary Facilities | SHPT
Sanitary Facilities | SHST
Sanitary Facilities | WCAC
Sanitary Facilities | WCPT
Sanitary Facilities | WCPU
Sanitary Facilities | WCST
Staff Amenities | BPROP
Staff Amenities | CHST-10
Staff Amenities | CHST-35
Staff Amenities | OVBR
Staff Amenities | OVES
Staff Amenities | SRM-15
Staff Amenities | SRM-35