## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Single line edit) | (Single line edit) | (Single line edit) | (Single line edit)
GYAH-60 | Gymnasium, 60m2 | 60 |  | Up to 13 patients/ hour; up to 4 staff | 8am to 6pm daily | Acoustic privacy is required | The Gymnasium provides for patient evaluation, rehabilitation exercise activities, therapy and ambulation training. An external outlook is desirable. The equipment to be used in this area will be dependent on the function of the gym and the Operational Policy. Acoustics: Acoustic privacy required. Body Protected electrical area

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No)
GYAH-60 | Gymnasium, 60m2 | Fabrics | 1000 | Floor finish | 1 |  | Vinyl | Standard slip resistant | Seamless, coved | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | Fabrics | 2000 | Skirting | 1 | cushioned vinyl optional | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | Fabrics | 3060 | Wall finish | 1 | to basin & sink, tiles also acceptable | Vinyl | Prefinished | Splashback | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | Fabrics | 5030 | Ceiling - Plasterboard | 1 | flush set plasterboard ceiling also acceptable | Plasterboard | Prefinished | Drop-in tiles, 600x1200 | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | Fabrics | 7001 | Windows | 1 | desirable |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | Fabrics | 8010 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | Fabrics | 8040 | Door protection | 1 | Equal to 'Acrovyn' | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | Fabrics | 9225 | Door - 1500mm | 1 | 1400 mm clear opening, lockable | Solid Core/ Glass | Paint | Double leaf, observation panel | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FE | FE-2800 | Basin - handwash, Type B | 1 | refer to BHWS (sim) |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
GYAH-60 | Gymnasium, 60m2 | FE | FE-4045 | Tapware - elbow mixer | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FE | FE-47890 | Sink & drainer - single, 930mmL | 1 | optional, hot water |  |  |  | No | No | Yes | Yes | Yes | Yes | Yes | No | No
GYAH-60 | Gymnasium, 60m2 | FE | FE-54520 | Telephone - handset, handsfree (WM) | 1 |  |  |  |  | No | Yes | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-1050 | Bench - laminate | 1 | optional |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-12450 | Locker - bedside | 2 | or trolley, to plinth spaces |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-1250 | Blind - Venetian | 3 | 1 to each external/ internal window, if provided |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-1325 | Mirror - safety glass | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-13645 | Steel mesh - framed, ceiling mount | 2 | to plinths, optional |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-13646 | Steel mesh - framed, wall mount | 2 | to plinths, optional |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-1650 | Chair - client | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-16780 | Parallel bars | 1 | min 5 metres long |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-17630 | Plinth | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-18170 | Pulley weights - wall mounted | 1 | optional |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-3350 | Clock - battery operated | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-4410 | Cupboard - under bench | 2 | optional |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-4430 | Cupboard - drawer unit | 1 | under bench, optional |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-4460 | Cupboard - wall mounted | 2 | over bench, optional |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-4600 | Curtain track - bed screen | 2 | to plinth spaces |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-5000 | Curtain - bed screen | 2 | to plinth spaces |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-5824 | Waste bin - general | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-6152 | Dispenser - disposable glove | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-6154 | Dispenser - paper/ hand towel | 2 | to basin & sink |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-6156 | Dispenser - soap | 2 | to basin & sink |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-6158 | Dispenser - soap antiseptic | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-7520 | Exercise bicycle | 2 | optional |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | FF | FF-7530 | Exercise stairs | 1 | optional |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | SE | S-1000 | Telephone: PABX | 1 | to wall phone |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | SE | S-1006 | Voice / Data outlet: double | 2 | 1 to each plinth space |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | SE | S-1006 | Voice / Data outlet: double | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | SE | S-1951 | Staff assist call | 3 |  |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | SE | S-6000 | General fluorescent | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | SE | S-6200 | Light switches | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | SE | S-8000 | Patient/ Staff call | 2 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | SE | S-8005 | Patient call handset | 2 | call button on the handset |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | SE | S-8010 | Staff/ Nurse assist call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | SE | S-8080 | Emergency call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | SE | S-9001 | GPO: Double | 9 | quantity will be determined by equipment to be used and Operational Policy |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | SE | S-9015 | GPO: Cleaner | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
GYAH-60 | Gymnasium, 60m2 | SE | S-9040 | Body protected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No