## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
GYAH-GP | Gymnasium, Group Therapy | Allied Health | Translation and QA Only | 105 | 2700 |  | 1 | 07.04.2026 |  | 7am to 6pm, daily (dependent on unit operating hours) | up to 15 patients;; 2-3 staff | The Gymnasium - Group Therapy provides space and facilities for patient evaluation, rehabilitation exercise activities, therapy and ambulation training in a group setting. An open area is typically provided for aerobic/movement exercises and may also provide space for group debriefing, discussion and education after sessions. | ~ An external outlook and ready access to outdoor areas is desirable. ~ The range of specialised exercise equipment, open exercise areas and number of clients / patients to be accommodated within a gymnasium will vary from unit to unit and will require confirmation to inform overall space requirements. ~ RCD protection is required to body protected areas in accordance with AS/NZS3003. Quantity and location dependent on selected equipment and circuiting arrangements. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
GYAH-GP | Gymnasium, Group Therapy | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
GYAH-GP | Gymnasium, Group Therapy | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
GYAH-GP | Gymnasium, Group Therapy | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to room side
GYAH-GP | Gymnasium, Group Therapy | Allied Health | D+W | DOHI-106 | DOOR: hinged, 1 1/2 leaves, 1600 clear opening, solid | 1 | 3 | Internal - Door 2 | [DWSC-027] optional, to equipment store
GYAH-GP | Gymnasium, Group Therapy | Allied Health | D+W | DOHI-145.01 | DOOR: hinged, 1 1/2 leaves, 1500 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | [DWGL-041]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 2 | 1 |  | [FIDI-001]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | FIGE-041 | STEEL MESH: framed, ceiling mounted | 1 | 3 |  | [FIRT-017] optional, to plinth
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | FIHR-029 | HOOK: equipment, wall mounted | 2 | 1 |  | [FIHR-029] to plinth
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | [FIHR-033] to plinth
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-047]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 2 | 1 |  | [FQBS-030] to arm ergometer
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | FQDW-134.02 | WORKSTATION: straight, adjustable height, 720H nom, 750D x 1200W | 2 | 1 |  | [FQDW-028] for arm ergometer
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1 |  | [FQGE-010] to plinth
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 1 | 1 |  | [FQSN-007] to plinth
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | JOSP-151 | JOINERY UNIT: bespoke, gymnasium, tall, equipment storage, open shelves | 1 | 1 |  | [FIJO-225]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | JOSP-152 | JOINERY UNIT: bespoke, gymnasium, tall, equipment storage, enclosed | 1 | 1 |  | [FIJO-227]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | MMAH-051 | EXERCISE MACHINE: stationary bicycle | 2 | 1 |  | [MMAH-002]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | MMAH-052 | EXERCISE MACHINE: stationary bicycle, recumbent | 1 | 1 |  | [MMAH-003]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | MMAH-061 | EXERCISE MACHINE: rowing | 1 | 1 |  | [MMAH-019]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | MMAH-066 | EXERCISE MACHINE: stepping | 1 | 1 |  | [MMAH-020]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | MMAH-071 | EXERCISE MACHINE: treadmill | 2 | 1 |  | [MMAH-027]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | MMAH-076 | EXERCISE MACHINE: ergometer, upper body | 2 | 1 |  | [MMAH-016]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | MMAH-146 | WEIGHTS: dumbbell set, with rack, floor standing | 1 | 1 |  | [FIHR-061]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FFE | MMAH-171 | PLINTH: treatment, electric | 1 | 1 |  | [MMAH-035]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FIN | CLTI-021.02 | CEILING: drop-in tiles, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-008]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 3 | 1 | Floor Skirting | [FLSK-010]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FIN | FLVY-122 | FLOOR FINISH: vinyl, seamless, inset, distance markings | 1 | 1 | Floor Finish 2 | [FLVY-010]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 2 | 1 | Wall Finish 2 | [WLWA-020]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] to plinth
GYAH-GP | Gymnasium, Group Therapy | Allied Health | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | SER | ELGP-201 | GPO: double, wall mounted | 3 | 1 |  | [ELGP-208] to plinth
GYAH-GP | Gymnasium, Group Therapy | Allied Health | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] quantity to suit equipment requirements
GYAH-GP | Gymnasium, Group Therapy | Allied Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
GYAH-GP | Gymnasium, Group Therapy | Allied Health | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 2 | 1 |  | [ITCL-008] 1 x to plinth, 1 x at entry door
GYAH-GP | Gymnasium, Group Therapy | Allied Health | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 2 | 1 |  | [ITCL-004] 1 x to plinth, 1 x at entry door
GYAH-GP | Gymnasium, Group Therapy | Allied Health | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 3 |  | [ITCL-028] optional, to plinth
GYAH-GP | Gymnasium, Group Therapy | Allied Health | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to telephone
GYAH-GP | Gymnasium, Group Therapy | Allied Health | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] to plinth