## Room Data
Standard Components - Room Data Sheet
Date of issue: 26.04.2021
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
HYDP | Hydrotherapy Pool | 260 | 7am to 8pm, daily | Up to 12 patients, 2-3 staff |  |  | The Hydrotherapy Pool is for patient therapy, rehabilitation and exercise under supervision. The pool size indicated is 15m x 6m (90m2 - not including pool surrounds). Pool and surrounds to comply with AS 3979 - Hydrotherapy Pools. Additional Design Considerations: Ready access is required to adequate change facilities for clients/patients and staff, including accessible showers and toilets. Emergency call points may be wall mounted and/or ceiling-suspended depending on the staffing model and local operational policies. Appropriate storage for aids and equipment will be required separately to the storage of pool maintenance equipment and chemicals. Depth 0.9m to 1.5 m with gradual slope. Depth at deep end may be reduced if paediatric use is likely to be frequent. Ramp access and stair access to be provided with handrails. Pool handrails are required and are not to be recessed. All stainless steel railing to be chlorine resistant. Temperature of water to be 33-34 degrees. Temperature of air to be no more than 6 degrees below water temperature. Wet deck - single channel. Water to be earthed. Internal pool surface and pool surrounds shown as tiled. Tiles or other suitable surface to be non-slip; ensure a high level of slip resistance to tiles on the ramp (vertical surfaces of tiling do not need to be slip resistant). Pool blanket is optional for insulation for energy conservation. Hydraulic hoist may be required; weight rating to be confirmed at project level to suit service requirements. Underwater pressure jets for therapeutic purposes are optional. Departmental planning to provide external windows is recommended. Disinfection system to be advised by expert consultant. Pool may be made available to the community after-hours and on the weekends. Careful consideration will need to be given to location, controlled access and security.

## Items
Standard Components - Items in room
Date of issue: 26.04.2021
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
HYDP | Hydrotherapy Pool | FA | FLGE-010 | FLOOR FINISH: tiles, ceramic, non-slip | 2
HYDP | Hydrotherapy Pool | FA | FLSK-004 | SKIRTING: tiles, coved, to match floor tiles | 12
HYDP | Hydrotherapy Pool | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 6
HYDP | Hydrotherapy Pool | FA | WLWA-011 | WALL FINISH: tiles, ceramic, glazed | 3 | to pool and all walls
HYDP | Hydrotherapy Pool | FA | CLFS-002 | CEILING: fibre cement, flush set, suspended, paint, washable | 1
HYDP | Hydrotherapy Pool | FA | DWWH-005 | WINDOW | 1 | desirable
HYDP | Hydrotherapy Pool | FA | DWOB-007 | OBSERVATION: internal window, alum/safety glass, powdercoat/paint | 4
HYDP | Hydrotherapy Pool | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 6 | to change rooms, cleaner's room, plant areas and alternate exit if required by BCA; lockable
HYDP | Hydrotherapy Pool | FA | DWGL-040 | DOOR: 1500mm c/o ,1 1/2 leaf, fully glazed, alum/safety glass, powdercoat/paint | 2 | to lobby/ waiting; lockable, restricted access
HYDP | Hydrotherapy Pool | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
HYDP | Hydrotherapy Pool | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1
HYDP | Hydrotherapy Pool | FFE | MMAH-017 | HOIST: pool, hydraulic | 1 | weight limit requirement to be confirmed dependent on service requirements
HYDP | Hydrotherapy Pool | FFE | MMAH-032 | BLANKET: pool, auto-operated | 1 | optional, power requirements dependent on selected model
HYDP | Hydrotherapy Pool | FFE | ITBU-009 | CONTROL UNIT: public address system | 1 | for announcements and music
HYDP | Hydrotherapy Pool | SE | ITBU-020 | PUBLIC ADDRESS SYSTEM | 1
HYDP | Hydrotherapy Pool | SE | HYTP-008 | OUTLET: cold water | 1 | for washing down concourse
HYDP | Hydrotherapy Pool | SE | HYDR-004 | DRAIN: floor waste | 16 | every 3-4 metres on concourse
HYDP | Hydrotherapy Pool | SE | ELBO-015 | SWITCH: light, single | 1
HYDP | Hydrotherapy Pool | SE | ITCL-004 | BUTTON: nurse call, emergency | 4 | 1 each side of pool
HYDP | Hydrotherapy Pool | SE | ELGP-106 | GPO: single, special, for equipment | 1 | optional, for motorised pool blanket
HYDP | Hydrotherapy Pool | SE | ELGP-113 | GPO: single, wall mounted, waterproof, RCD protected | 4