## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
HYDP | Hydrotherapy Pool | Allied Health | Translation and QA Only | 260 | 5479 |  | 5 | 07.04.2026 |  | 7am to 6pm, daily (dependent on unit operating hours) | up to 12 patients;; 2-3 staff | The Hydrotherapy Pool is for patient therapy, rehabilitation and exercise under supervision. | ~ The pool size indicated is 15m x 6m (90m2 - not including pool surrounds). Pool and surrounds to comply with AS 3979 - Hydrotherapy Pools. ~ Ready access is required to adequate change facilities for clients/patients and staff, including accessible showers and toilets. ~ Emergency call points may be wall mounted and/or ceiling-suspended depending on the staffing model and local operational policies. ~ Appropriate storage for aids and equipment will be required separately to the storage of pool maintenance equipment and chemicals. ~ Depth 0.9m to 1.5 m with gradual slope. Depth at deep end may be reduced if paediatric use is likely to be frequent. ~ Ramp access and stair access to be provided with handrails. Pool handrails are required and are not to be recessed. All stainless steel railing to be chlorine resistant. ~ Temperature of water to be 33-34 degrees. Temperature of air to be no more than 6 degrees below water temperature. ~ Wet deck - single channel. ~ Water to be earthed. ~ Internal pool surface and pool surrounds shown as tiled. Tiles or other suitable surface to be non-slip; ensure a high level of slip resistance to tiles on the ramp (vertical surfaces of tiling do not need to be slip resistant). ~ Pool blanket is optional for insulation for energy conservation. ~ Hydraulic hoist may be required; weight rating to be confirmed at project level to suit service requirements. ~ Underwater pressure jets for therapeutic purposes are optional. ~ Departmental planning to provide external windows is recommended. ~ Disinfection system to be advised by expert consultant. ~ Pool may be made available to the community after-hours and on the weekends. Careful consideration will need to be given to location, controlled access and security. | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 3 | External - Door 2 | [DWPR-001] to external side
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 6 | [DWPR-001] to plant room side
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to pool side
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 3 | [DWPR-005] to room side
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 4 | [DWPR-005] to pool side
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 5 | [DWPR-005] to pool side
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 6 | [DWPR-005] to pool side
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | External - Door 2 | [DWPR-005] to pool side
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to change room side
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 3 | [DWPR-005] to change room side
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 4 | [DWPR-005] to cleaner's room side
HYDP | Hydrotherapy Pool | Allied Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 5 | [DWPR-005] to equipment room side
HYDP | Hydrotherapy Pool | Allied Health | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 2 | [DWSC-003] to female change room
HYDP | Hydrotherapy Pool | Allied Health | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 3 | [DWSC-003] to male change room
HYDP | Hydrotherapy Pool | Allied Health | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 4 | [DWSC-003] to cleaner's room
HYDP | Hydrotherapy Pool | Allied Health | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 5 | [DWSC-003] to pool equipment room
HYDP | Hydrotherapy Pool | Allied Health | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 6 | [DWSC-003] to pool plant room
HYDP | Hydrotherapy Pool | Allied Health | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 3 | External - Door 2 | [DWSC-003] optional, for alternate external emergency exit; may be required by building code
HYDP | Hydrotherapy Pool | Allied Health | D+W | DOHI-165.01 | DOOR: hinged, 1 1/2 leaves, 1500 clear opening, fully glazed, framed | 1 | 1 | Internal - Door 1 | [DWGL-040] to lobby/ waiting; lockable, restricted access
HYDP | Hydrotherapy Pool | Allied Health | D+W | DOHI-165.01 | DOOR: hinged, 1 1/2 leaves, 1500 clear opening, fully glazed, framed | 1 | 1 | External - Door 1 | [DWGL-040] external emergency exit
HYDP | Hydrotherapy Pool | Allied Health | D+W | WIFX-007.01 | WINDOW: fixed, internal, single glazed, sill at 900H | 1 | 1 | Internal - Window 1 | [DWOB-007]
HYDP | Hydrotherapy Pool | Allied Health | D+W | WIFX-007.01 | WINDOW: fixed, internal, single glazed, sill at 900H | 1 | 1 | Internal - Window 2 | [DWOB-007]
HYDP | Hydrotherapy Pool | Allied Health | D+W | WIFX-007.01 | WINDOW: fixed, internal, single glazed, sill at 900H | 1 | 1 | Internal - Window 3 | [DWOB-007]
HYDP | Hydrotherapy Pool | Allied Health | D+W | WIFX-007.01 | WINDOW: fixed, internal, single glazed, sill at 900H | 1 | 1 | Internal - Window 4 | [DWOB-007]
HYDP | Hydrotherapy Pool | Allied Health | D+W | WIFX-157.01 | WINDOW: fixed, external, double glazed, sill at 900H | 1 | 1 | External - Window 2 | [DWWH-005] desirable
HYDP | Hydrotherapy Pool | Allied Health | D+W | WIFX-157.01 | WINDOW: fixed, external, double glazed, sill at 900H | 1 | 1 | External - Window 1 | [DWWH-005] desirable
HYDP | Hydrotherapy Pool | Allied Health | D+W | WIFX-163.01 | WINDOW: fixed, external, double glazed, sill at 1800H | 1 | 1 | External - Window 3 | [DWWH-005] desirable
HYDP | Hydrotherapy Pool | Allied Health | D+W | WIFX-163.01 | WINDOW: fixed, external, double glazed, sill at 1800H | 1 | 1 | External - Window 4 | [DWWH-005] desirable
HYDP | Hydrotherapy Pool | Allied Health | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
HYDP | Hydrotherapy Pool | Allied Health | FFE | MMAH-302 | POOL COVER: hydrotherapy, powered, on roller, fixed | 1 | 3 |  | [MMAH-032] optional, power requirements dependent on selected model
HYDP | Hydrotherapy Pool | Allied Health | FFE | MMBE-301 | LIFTER: patient hoist, seated pool transfer, hydrotherapy, fixed, floor mounted | 1 | 1 |  | [MMAH-017] weight limit requirement to be confirmed dependent on service requirements
HYDP | Hydrotherapy Pool | Allied Health | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
HYDP | Hydrotherapy Pool | Allied Health | FIN | CLFI-001 | CEILING FINISH: paint | 1 | 1 | Ceiling Finish 2
HYDP | Hydrotherapy Pool | Allied Health | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-002]
HYDP | Hydrotherapy Pool | Allied Health | FIN | FLSK-073 | SKIRTING: tiles, to match floor tiles, coved | 12 | 1 | Floor Skirting | [FLSK-004]
HYDP | Hydrotherapy Pool | Allied Health | FIN | FLTI-005 | FLOOR FINISH: tiles, ceramic, non-slip, wet area, barefoot | 2 | 1 | Floor Finish 2 | [FLGE-010]
HYDP | Hydrotherapy Pool | Allied Health | FIN | WLFI-021 | WALL FINISH: tiles, ceramic | 3 | 1 | Wall Finish 1 | [WLWA-011] to pool and all walls
HYDP | Hydrotherapy Pool | Allied Health | SER | ELGP-104 | GPO: single, wall mounted, waterproof, power available indicator | 4 | 1 |  | [ELGP-113]
HYDP | Hydrotherapy Pool | Allied Health | SER | ELGP-191 | GPO: single, special, for equipment, wall mounted | 1 | 3 |  | [ELGP-106] optional, for motorised pool blanket
HYDP | Hydrotherapy Pool | Allied Health | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
HYDP | Hydrotherapy Pool | Allied Health | SER | HYDR-021 | DRAIN: floor waste, round | 16 | 1 |  | [HYDR-004] every 3-4 metres on concourse
HYDP | Hydrotherapy Pool | Allied Health | SER | HYTP-431 | OUTLET: water, cold | 1 | 1 |  | [HYTP-008] for washing down concourse
HYDP | Hydrotherapy Pool | Allied Health | SER | ITBU-131 | HEAD END: public address system | 1 | 1 |  | [ITBU-020]
HYDP | Hydrotherapy Pool | Allied Health | SER | ITBU-132 | CONTROL PANEL: public address system | 1 | 1 |  | [ITBU-009] for announcements and music
HYDP | Hydrotherapy Pool | Allied Health | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 4 | 1 |  | [ITCL-004] 1 each side of pool