## Room Data
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Acoustics | Description / Special Requirements
INTF-MH | Interview Room - Mental Health | 14 | Varies | 1 Patient; 1-2 staff; 1-2 visitors | Sound attenuation high; acoustic privacy is required | The Interview Room - Mental Health provides a room that can be used by patients with mental health conditions for interviews or counselling. The room has been configured to reduce risks to both staff and patients. A secondary egress door is shown.All fittings must be of a type manufactured as anti ligature and installed in accordance with manufacturer's instructions. Door and joinery hardware and any engineering services outlets must not provide ligature points and must be tamper proof. All glass must be Grade A safety glass to comply with AS1288 and AS/ANZ 2208, specifically toughened laminated glass of min. 14.28mm thickness or equivalent approved. Consider location of wi-fi access points to ensure strong wi-fi coverage is provided for mobile duress functions. Jurisdictional policy to be read in conjunction with guidelines.

## Items
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
INTF-MH | Interview Room - Mental Health | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1 |  | No | No | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 |  | No | No | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | FA | DWGL-007 | DOOR: 910mm c/o, single leaf, observation panel, solid core/safety glass, paint | 2 | privacy film to be applied to obs panel in second egress door | No | No | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2 | optional | No | No | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 4 | optional | No | No | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | FFE | DWWD-002 | BLIND: holland | 1 | optional, roller blind in community areas, integral venetian required for hospital areas | No | No | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | FA | DWWH-005 | WINDOW | 1 | optional | No | No | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | SE | ELBO-015 | SWITCH: light, single | 1 | lighting to have controlled switching to create low stimulus environment | No | No | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | SE | ELGP-208 | GPO: double, wall mounted | 2 |  | No | No | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | FFE | FIBM-016 | NOTICEBOARD/WHITEBOARD: fixed, combined unit | 1 |  | No | No | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 1 |  | No | No | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | FFE | FQBS-018 | CHAIR: office, ergonomic | 1 |  | No | No | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | FFE | FQBS-054 | STOOL: ottoman | 1 |  | No | No | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | FFE | FQBS-056 | CHAIR: tub, mental health | 3 |  | No | No | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | FFE | FQDW-040 | DESK: fixed height, 1200W x 750D x 720H | 1 |  | No | No | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | FFE | FQGE-002 | ARTWORK | 1 |  | No | No | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 |  | No | Yes | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 |  | Yes | Yes | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 |  | No | Yes | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | SE | ITSE-006 | BUTTON: duress, fixed | 2 | optional, depends on jurisdictional policy; mobile duress preferred | No | No | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | SE | ITSE-038 | READER: access control, general | 1 | optional | No | No | No | No | No | No | No | No | No
INTF-MH | Interview Room - Mental Health | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No