## Room Template Data
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Website - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
INTV-MH | Interview Room - Mental Health | Mental Health | Full AHIA Review | 14 | 2700 | INTF-MH | 3 | 31.03.2026 | https://healthfacilityguidelines.com.au/component/interview-room-mental-health/?fullscreen=true&utm_source=project-link&rev=3 | Up to 24 hours (dependent on unit operating hours) | up to 6 persons;;; | The Interview Room - Mental Health (may be referred to on projects as a Dialogue Room) provides the space and amenities for interviews, counselling, collaborative care planning and small support network discussions within a Mental Health Unit. | ~ Unique requirements will exist in different care settings (i.e. intensive care, high dependency, acute, sub-acute, non-acute, units for children and adolescents, unit for older persons, etc.) and confirmation of the factors to be considered to meet the different service requirements and patient cohorts is required at project level. ~ All fittings and fixtures used must be of a type manufactured and marketed as anti-ligature. Requirements for the selection of suitable finishes, hardware, fixtures and fittings (including any weight limits for load release for certain fixtures) must be confirmed at project level based on service requirements, patient safety policies, local design guidance, risk assessments and confirmation of operational models. This includes the door, door hardware, joinery surfaces, joinery hardware, engineering services outlets and any ceiling mounted fixtures and services. All tamper proof and anti-ligature items must be installed in accordance with their manufacturer's instructions. ~ Where an accessible room is required to be provided, in order for the room to meet accessibility requirements, anti-ligature fittings may require a performance solution. This must be considered and addressed at project level with appropriate accessibility and building code consultants to meet applicable legislation and standards. ~ All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, sub-acute, acute, high dependency, intensive care, etc.). ~ Window size and minimum sill height are to be confirmed at project level. Access to natural daylight and an external outlook are desirable. Consider placement of windows and room orientation to suit privacy requirements. The type of window covering (e.g. roller blind, integral venetians, etc.) and associated controls are also to be confirmed at project level. ~ Doors should be selected to support safety, dignity and wellbeing. Selections should be non-institutional in appearance to the extent possible. It is recommended that the door set is selected as a full assembly to ensure the leaf, frame and hardware are coordinated and meet all tamper proof, anti-ligature and anti-barricade requirements when used together. Inclusion and size of a vision panel to be confirmed to suit service requirements. Privacy film may be applied to the vision panel as required. It is recommended that projects review in-situ installations/prototypes to confirm which solution addresses all requirements of their mental health environment. ~ A second door is required for safety and security. The location of the second door will be dependent on the overall floor plan and availability of an appropriate area to egress. ~ The ceiling height is indicated as 2.7m. Based on a risk assessment, the ceiling height is to be confirmed at a project level. Selection of FF&E (lounges, chairs, tables, etc.) is to be considered in conjunction with assessing ceiling height to ensure consumers cannot reach or cause damage to the ceiling or services located on the ceiling. A plywood backing to the ceiling finish may be considered to provide a robust, impact resistance surface, particularly in high dependency and intensive care areas. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. The location of Wi-Fi access points is to be carefully considered to ensure strong coverage is provided for mobile duress functions. ~ The selection of finishes in rooms for mental health units is to be carefully considered to support the provision of a welcoming, warm and therapeutic atmosphere. Interior design should aim to eliminate an institutional feel. Flooring and skirting selections are to be considered at project level based on risk assessment for provision of alternative options (e.g. timber/MDF skirting in lieu of coved skirtings). ~ Provision of a workstation is dependent on service requirements (e.g. for computer-based assessments to be undertaken). Impact on furniture arrangement when a workstation is included must be considered to support a positive dynamic between staff and consumers and encourage participation of consumers as equal partners in care. ~ Nearby access to a beverage bay or water fountain is recommended. | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE

## Items In Room Template
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 31
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AFDFI-026 | DOOR GLAZING FINISH: vision panel, privacy film | 1 | 1 | Internal - Door 1 | optional; as required to suit privacy requirements
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | to room side
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to room side
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | to corridor side as required
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | to corridor side as required
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 2 | optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 3 | External - Window 1
INTV-MH | Interview Room - Mental Health | Mental Health | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice | square set cornice acceptable if flush set ceiling is provided
INTV-MH | Interview Room - Mental Health | Mental Health | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | if tamper proof and anti-ligature finish required flush set ceiling to be provided
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | DOHI-003.03 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature | 1 | 1 | Internal - Door 2 | secondary egress
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | DOHI-013.08 | DOOR: hinged, 1 leaf, 900 clear opening, solid, anti-ligature, standard vision panel | 1 | 1 | Internal - Door 1 | requirements for glazing in vision panel to be confirmed to suit the mental health environment
INTV-MH | Interview Room - Mental Health | Mental Health | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | SER | ELSW-001 | SWITCH: light | 1 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | FIBM-020 | WHITEBOARD: fixed, magnetic, tamper proof, anti-ligature | 1 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | FIBM-057 | NOTICE BOARD: fixed, fabric covered, tamper proof, anti-ligature | 1 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1
INTV-MH | Interview Room - Mental Health | Mental Health | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 6 | 1 | Floor Skirting
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | FQBS-111 | CHAIR: visitor, mental health | 2 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | FQBS-352 | LOUNGE: 2 seat | 1 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | FQBS-354 | LOUNGE: ottoman | 2 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | FQDW-104.02 | WORKSTATION: straight, fixed height, 720H, 750D x 1200W | 1 | 3 |  | optional, dependent on operational service requirements
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | FQGE-002 | ARTWORK: wall mounted | 1 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | 1
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 3 |  | optional, dependent on operational service requirements
INTV-MH | Interview Room - Mental Health | Mental Health | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 3 |  | optional, dependent on operational service requirements
INTV-MH | Interview Room - Mental Health | Mental Health | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 3
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 2 | optional; provision to suit security and egress requirements
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 1 | Internal - Door 1 | optional; provision to suit security and egress requirements
INTV-MH | Interview Room - Mental Health | Mental Health | D+W | WIFX-156.01 | WINDOW: fixed, external, double glazed, sill at 750H | 1 | 3 | External - Window 1 | optional; natural light and external outlook is desirable; consider placement and room orientation for patient privacy; requirements for glazing to be confirmed to suit the mental health environment
INTV-MH | Interview Room - Mental Health | Mental Health | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 4 | 1 | Wall Finish 1