## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
INTV | Interview Room | Ambulatory Care | Translation and QA Only | 12 | 2700 | INTF | 5 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 8 persons;;; | The Interview Room provides space for confidential discussion and/or counselling between staff, patients and/or family members where required. The Interview Room may also be used as a multipurpose room for small staff groups or discussions. | ~ An external outlook is desirable. Assumes staff will bring their own devices as required. ~ A second door may be required for staff safety and security; the location of the second door will be dependent on the availability an appropriate area to egress. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
INTV | Interview Room | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
INTV | Interview Room | Ambulatory Care | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
INTV | Interview Room | Ambulatory Care | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
INTV | Interview Room | Ambulatory Care | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005]
INTV | Interview Room | Ambulatory Care | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 | Internal - Door 2 | [ITSE-038] optional to second egress door
INTV | Interview Room | Ambulatory Care | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 3 | Internal - Door 2 | [DWGL-005] optional, for staff egress
INTV | Interview Room | Ambulatory Care | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
INTV | Interview Room | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
INTV | Interview Room | Ambulatory Care | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
INTV | Interview Room | Ambulatory Care | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 3 | Internal - Door 2 | [DWPR-001] to room side
INTV | Interview Room | Ambulatory Care | D+W | WIFX-057.01 | WINDOW: fixed, internal, double glazed, sill at 900H | 1 | 1 | External - Window 1 | [DWWH-005]
INTV | Interview Room | Ambulatory Care | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
INTV | Interview Room | Ambulatory Care | FFE | FQBS-251 | ARMCHAIR: visitor, clinical areas | 1 | 1 |  | [FQBS-010]
INTV | Interview Room | Ambulatory Care | FFE | FQGE-002 | ARTWORK: wall mounted | 1 | 3 |  | [FQGE-002] optional
INTV | Interview Room | Ambulatory Care | FFE | FQTA-202 | TABLE: square, 450H, 600L | 2 | 1 |  | [FQTA-075]
INTV | Interview Room | Ambulatory Care | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-050]
INTV | Interview Room | Ambulatory Care | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 4 | 1 |  | [FQBS-058]
INTV | Interview Room | Ambulatory Care | FFE | FQBS-352 | LOUNGE: 2 seat | 1 | 1 |  | [FQBS-041]
INTV | Interview Room | Ambulatory Care | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
INTV | Interview Room | Ambulatory Care | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
INTV | Interview Room | Ambulatory Care | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1 | [FLCP-006]
INTV | Interview Room | Ambulatory Care | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 6 | 1 | Floor Skirting | [FLSK-009] aluminum skirting is also acceptable
INTV | Interview Room | Ambulatory Care | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
INTV | Interview Room | Ambulatory Care | SER | ELGP-201.01 | GPO: double, wall mounted, horizontal | 2 | 1 |  | [ELGP-208]
INTV | Interview Room | Ambulatory Care | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
INTV | Interview Room | Ambulatory Care | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 3 |  | [ITCL-008] optional, + indicator button & light
INTV | Interview Room | Ambulatory Care | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 3 |  | [ITCL-004] optional, + indicator button & light
INTV | Interview Room | Ambulatory Care | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | [ITIN-026]
INTV | Interview Room | Ambulatory Care | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]
INTV | Interview Room | Ambulatory Care | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]