## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | Translation and QA Only | 21 | 2700 |  | 1 | 07.04.2026 |  | 8am to 6pm, Mon - Fri (dependent on unit operating hours) | up to 5 staff | The Linear Accelerator Control room is located adjacent to the Treatment Room for remote control of equipment with audio and visual contact with the patient via cameras, speakers and microphones. Each Treatment Room requires a Control Room. | ~ Cable pathways for services between the Control room to the Treatment Room must be established and coordinated prior to construction. Radiation shielding is to be as advised by a Radiation Consultant. ~ Air conditioning to provide comfort conditions; high equipment loads shall be accounted for. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements. Small UPS units are normally required as a minimum to support control and operating equipment. In some cases, these are supplied with the medical equipment. Other emergency power and UPS requirements to be confirmed based on risk assessment considering the impact of a power outage on patient care/safety. ~ Cable management and the potential for computers to be consolidated into a rack (either within the room or in a dedicated, collocated air conditioned room/cupboard) to be determined at project level. ~ Provision of a height adjustable workstation may be considered depending on local policies and staff accessibility requirements. | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 3 | Internal - Door 1 | [DWPR-001] to room side
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 3 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 3 | Internal - Door 1 | [DWSC-003] optional
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 2 | 1 |  | [FIHR-067] to patient observation monitors
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | FQBS-171 | CHAIR: office, ergonomic | 5 | 1 |  | [FQBS-018]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | ITAV-146 | MICROPHONE: AV system, surface mounted, gooseneck | 1 | 1 |  | [ITAV-014]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | ITAV-152 | SPEAKER: AV system, ceiling recessed | 1 | 1 |  | [ITAV-057] may be bench mounted, or integrated with microphone
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | ITCL-381 | DISPLAY SCREEN: patient observation | 2 | 1 |  | [ITNE-074]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-049]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | ITNE-102 | COMPUTER: dual display screens, central processing unit (CPU), keyboard and mouse, desktop | 2 | 1 |  | [ITNE-071] for access to local network including patient records and images for planning and reporting
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1 |  | [ITNE-067] for patient observation cameras to control pan, tilt and zoom; may be custom control depending on camera system
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | JOBE-061 | BENCH: 750D, laminate | 2 | 1 |  | [FIJO-031]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | JOBE-211 | BENCH SUPPORT: bracket | 5 | 1 |  | [FIHR-080] legs are also acceptable, quantity to be confirmed to achieve required support, ensure location does not impact leg clearance at workstations
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | JOBE-221 | BENCH SUPPORT: end panel | 2 | 1 |  | [FIJO-213]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | JOBE-251 | CAP: cable access | 8 | 1 |  | [FIJO-099]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | JOCU-121 | CUPBOARD: wall mounted, double door | 5 | 1 |  | [FIJO-145]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead is also acceptable
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | MMRA-011 | CONTROL CONSOLE: linear accelerator, dual display screens, keyboard and mouse, control unit, microphone and speaker, desktop | 1 | 1 |  | [MMRA-010]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | MMRA-016 | COMPUTER: linear accelerator, central processing unit (CPU) | 6 | 1 |  | [MMRA-009] quantity to be confirmed based on vendor and equipment requirements; current provision allows for 1 x linear accelerator control system, 1 x record and verify system, and 2-4 x imaging and patient set up systems (e.g. gating and patient positioning).
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | MMRA-021 | SYSTEM CABINET: linear accelerator | 1 | 1 |  | [MMRA-007] size, configuration and location to be confirmed by vendor
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FFE | MMRA-191 | ACCESS PANEL: penetration, medical physics port | 1 | 1 |  | [MMRA-006]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 9 | 1 | Floor Skirting | [FLSK-010]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | FIN | WLFI-001 | WALL FINISH: paint | 5 | 1 | Wall Finish 1 | [WLWA-004]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ELGP-191 | GPO: single, special, for equipment, wall mounted | 1 | 1 |  | [ELGP-106] to linear accelerator computer cabinet
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ELGP-201 | GPO: double, wall mounted | 10 | 1 |  | [ELGP-208]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 14 | 1 |  | [ELGP-223] quantity to suit computer and display screen requirements
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ELPR-071 | RCD: residual current device, wall mounted | 3 | 1 |  | [ELPR-006]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 1 | 1 |  | [ELBO-001] may be integral to linear accelerator control console
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | 1 |  | [ITIN-026]
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 8 | 1 |  | [ITIN-036] quantity to suit computer and display screen requirements
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ITIN-056 | OUTLET: data, USB, wall mounted | 1 | 1 |  | [ITIN-055] connection for music to bunker
LINAC-CR | Linear Accelerator Control Room | Radiation Oncology | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]