## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | Translation and QA Only | 165 | 3000 |  | 1 | 07.04.2026 |  | 8am to 6pm, Mon - Fri (dependent on unit operating hours) | 1 patient;; up to 4 staff | The Linear Accelerator Treatment Room provides space and facilities for the treatment of patients requiring external beam radiation therapy (EBRT). A collocated Control Room is required for the remote operation of equipment. | ~ Cable pathways for services between the Control Room, Modulator Room and Treatment Room must be established and coordinated prior to construction and developed based on vendor and physics requirements. Equipment is to be installed to manufacturer's specifications with sufficient clearances for maintenance access. ~ The Treatment Room must be adequately shielded to ensure that radiation doses to surrounding areas do not exceed radiation dose limits and satisfy design/dose constraints, including the provision of a maze entry or shielded door. Radiation shielding is to be as advised by a qualified Radiation Consultant to suit the practice, workload and equipment procured, and all shielding on the Standard Component is indicative only. ~ The modulator may need to be accommodated within the Treatment Room. If so, this will be concealed by a wall, with a door for access. Depending on the quality of the power supply at a site, a power conditioner may be required and is typically located with the modulator. Additional noise from this equipment should also be accounted for with acoustic treatment. ~ Visibility of the Treatment Room from exit and via observation cameras is required to ensure all persons are clear of the room before treatment commences. A last person out button is to be provided, as well as a sensor gate and/or physical gate at the entry of the maze. A Beam-On/Off light system is required at the entry to be illuminated when treatment begins/ends. ~ Additional medical gases may be provided (including additional oxygen, additional suction, nitrous oxide and scavenge) depending on clinical requirements such as the provision of anaesthetic services. ~ Acoustic requirements will vary depending on the equipment procured and its proximity to the patient treatment area. For patient and staff comfort, acoustics should be considered to reduce the impact of noise from the equipment. ~ Dimmable lights are to be provided and are to be placed to avoid glare to patients. ~ Back lit ceiling artwork may be installed for patient comfort and speakers and connections should be provided to allow music to be played and controlled individually for each bunker. ~ Air conditioning is to be provided to control the room temperature and humidity to meet the equipment suppliers requirements; high equipment loads shall be accounted for. Air conditioning equipment shall be located outside of this room with ductwork to be installed to follow the entry maze with any penetrations considered to ensure radiation protection. Where possible, it is preferred that ductwork in the ceiling is designed to the perimeter of room for future flexibility to provide ceiling mounted equipment. ~ Cooling shall be provided to the linear accelerator equipment in the form of chilled water to meet the suppliers requirements, independent chiller equipment is preferred. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements. Small UPS units are normally required as a minimum to support control and operating equipment. In some cases, these are supplied with the medical equipment. Other emergency power and UPS requirements to be confirmed based on risk assessment considering the impact of a power outage on patient care/safety. ~ A mix of respiratory gating, surface guidance, motion management and/or patient position technologies may be provided depending on clinical/service requirements. The provision of these technologies is to be confirmed by the project and may have additional requirements including additional power/data, water cooling, heat load, possible increased set down, increased number of trenches/conduits, space requirements for computer cabinets in control room and additional penetrations through the suspended ceiling. Requirements to be confirmed with vendors. ~ Allow sufficient distance between the isocentre of the machine and primary shielding wall for the flexibility to provide specialised treatments, e.g. Total Body Irradiation (TBI), depending on service requirements. | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | D+W | DOSP-202 | GATE: hinged, 1 leaf, 900 clear opening | 1 | 1 | Internal - Door 1 | [DWGE-013]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIDI-181 | DISPENSER: cleaning wipes, wall mounted | 1 | 1 |  | [FIDI-006]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1 |  | [FIHR-019]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIHR-214 | BRACKET: computer display screen, single, articulated, ceiling mounted | 2 | 1 |  | [FIHR-004]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIHR-322 | BRACKET: keyboard and mouse, fixed height, wall mounted | 1 | 1 |  | [FIHR-093]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | [FIHR-067]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | [MMGE-048]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FQCL-251 | TROLLEY: clean linen, small | 1 | 1 |  | [MMGE-110]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | ITAV-141 | MICROPHONE: AV system, ceiling mounted | 2 | 1 |  | [ITAV-010]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | ITAV-152 | SPEAKER: AV system, ceiling recessed | 2 | 1 |  | [ITAV-057] for patient's own music, individual to each bunker from control room, hearing loop required to speakers
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | ITCL-351 | DISPLAY SCREEN: patient treatment information | 1 | 1 |  | [ITNE-073] wall mounted
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | ITCL-351 | DISPLAY SCREEN: patient treatment information | 1 | 1 |  | [MMRA-013] radiotherapy information, ceiling mounted
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | ITCL-431 | CAMERA: patient observation, ceiling mounted | 6 | 1 |  | [ITCL-012 + FIHR-077] 1 x optional, for total body irradiation or visualisation of additional monitoring equipment, pan, tilt and zoom (PTZ) capability is required, quantity to be based on equipment and service requirements
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007] workstation on wheels is also acceptable
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | ITNE-121 | COMPUTER: single display screen, all-in-one | 1 | 1 |  | [ITNE-066]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1 |  | [ITNE-067] to wall mounted computer, may be wireless
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | JOBE-031 | BENCH: 600D, laminate | 3 | 1 |  | [FIJO-058]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | JOCU-201 | CUPBOARD: under bench, single door | 1 | 1 |  | [FIJO-140]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | JOCU-221 | CUPBOARD: under bench, double door | 3 | 1 |  | [FIJO-135]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | [FIJO-212] plasterboard bulkhead is also acceptable
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | JOSP-031 | JOINERY UNIT: bespoke, radiotherapy, tall, applicator storage | 1 | 1 |  | [FIJO-165] custom joinery is required for vendor specific electron cones, including sliding rails, shelving to be reinforced for electron shields
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | JOSP-032 | JOINERY UNIT: bespoke, radiotherapy, tall, horizontal patient device storage | 3 | 1 |  | [FIJO-166] wide span shelving to be reinforced
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | JOSP-033 | JOINERY UNIT: bespoke, radiotherapy, tall, vertical patient device storage | 2 | 1 |  | [FIJO-167]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | JOSP-041 | JOINERY UNIT: bespoke, radiotherapy, wall mounted, laser enclosure | 3 | 1 |  | [FIJO-231]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | [MMGE-100]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | MMRA-001 | RADIOTHERAPY DEVICE: treatment, linear accelerator | 1 | 1 |  | [MMRA-004]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | MMRA-031 | SENSOR: entry detection, light curtain, radiotherapy bunker, | 1 | 1 |  | [MMRA-012]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | MMRA-041 | LASER: patient positioning, radiotherapy, overhead | 1 | 1 |  | [MMRA-015]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | MMRA-044 | LASER: patient positioning, radiotherapy, lateral, MRI compatible | 2 | 1 |  | [MMRA-016]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | MMRA-046 | LASER: patient positioning, radiotherapy, sagittal, MRI compatible | 1 | 1 |  | [MMRA-017]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | MMRA-071 | DEVICE: surface guided radiation therapy system, ceiling mounted | 3 | 1 |  | [MMRA-008 + FIHR-089] as required for respiratory gating / motion management / surface guidance systems, to suit service requirements
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | MMRA-106 | DEVICE: tester, radiotherapy, daily QA | 1 | 1 |  | [MMRA-011]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FFE | MMRA-191 | ACCESS PANEL: penetration, medical physics port | 1 | 1 |  | [MMRA-006]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FIN | CLFI-003 | CEILING FINISH: paint, sterile areas | 1 | 1 | Ceiling Finish 2 | [CLFS-005]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-005]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 3 | [CLTI-002] inset area above machine as requried
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 18 | 1 | Floor Skirting | [FLSK-010]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FIN | FLVY-103 | FLOOR FINISH: vinyl, seamless, standard slip resistance, static dissipative | 1 | 1 | Floor Finish 1 | [FLVY-001] floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FIN | WLFI-001 | WALL FINISH: paint | 14 | 1 | Wall Finish 1 | [WLWA-004]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FIN | WLFI-011.01 | WALL FINISH: vinyl, to 900 AFFL | 16 | 1 | Wall Finish 2 | [WLWA-022]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | [WLWA-007] to basin
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | FIN | WLPR-006 | WALL PROTECTION: corner guards | 9 | 1 | Wall Protection | [WLPR-006]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 3 | 1 | Panel 1 | [ELGP-122]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1 | [ELPR-006]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1 | [MGAS-062]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1 | [MMGE-002]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 1 | 1 |  | [ELGP-123]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ELGP-136 | GPO: single, emergency power, ceiling mounted | 12 | 1 |  | [ELGP-125] 1 x to ceiling mounted laser, 1 x optional, to additional patient observation camera if provided
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 5 | 1 |  | [ELGP-220.1] to wall mounted lasers
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 4 | 1 |  | [ELGP-223]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ELPR-071 | RCD: residual current device, wall mounted | 4 | 1 |  | [ELPR-006]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-010]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ELSW-121 | BUTTON: emergency stop, wall mounted | 4 | 1 |  | [ELBO-001]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ELSW-131 | BUTTON: last person out | 1 | 1 |  | [ELBO-019]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 11 | 3 |  | [ITIN-011] 1 x optional, to additional patient observation camera if provided
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3 | 1 |  | [ITIN-016]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | LIFX-192 | LIGHT: feature, backlit panels, ceiling mounted | 2 | 1 |  | [LIFX-038]
LINAC | Linear Accelerator Treatment Room | Radiation Oncology | SER | LIFX-214 | LIGHT: illuminated sign, beam on/off | 1 | 1 |  | [LIFX-004]