## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | Translation and QA Only | 10 | 2700 | LNPT-10 | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 6 patients / visitors;; 1-2 staff intermittently | The Patient Lounge provides an environment away from clinical areas and/or patient bedrooms for patients and visitors to meet and socialise. It is an area where family groups can visit together with patients. | ~ A range of occupants will need to be accommodated including adults, children, able-bodied people as well as people with disabilities. ~ The size of lounge areas can vary depending on service requirements; add 1.2m2 per additional person and allow 1.5m2 for additional wheelchair spaces as required. ~ Access for a patient lifter or patient bed may be required depending on patient cohort and service requirements. ~ The Patient Lounge is often located in close proximity to or combined with a Bay - Beverage. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. Patient to nurse call button and handset is optional and may be provided in units where high patient observation is required. ~ Duress provision will be dependent on service requirements. ~ Provision of a hearing augmentation system may be required depending on television and amplification system provided. ~ Furniture shown in this Standard Component is indicative and items selected will vary depending on patient cohort. Considerations regarding furniture include assessing the weight rating of all seating, including for bariatric capacity as required, providing a mix of chairs with and without arms to support patient mobility, and providing built-in furniture or securing furniture where there may be safety/security concerns. ~ Room may be designed to be open to a corridor. Additional transfer of noise to adjacent patient care areas to be considered if room is not enclosed. ~ The display of artwork and cultural assets will be guided by the facility. A rail display system may be considered to minimise risks and allow for flexibility in display. Ease of cleaning for infection prevention and control also needs to be considered when selecting artwork. ~ Natural light and external outlook is essential. | TRUE | FALSE | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | [DWGL-002]
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | D+W | WIFX-158.01 | WINDOW: fixed, external, double glazed, sill at 1050H | 1 | 1 | External - Window 1 | [DWWH-005] natural light and external outlook is essential
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006]
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FFE | FQBS-352 | LOUNGE: 2 seat | 1 | 1 |  | [FQBS-043] furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FFE | FQGE-002 | ARTWORK: wall mounted | 2 | 1 |  | [FQGE-002]
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FFE | FQTA-202 | TABLE: square, 450H, 600L | 2 | 1 |  | [FQTA-075] furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FFE | MMGE-019 | CHAIR: patient | 2 | 1 |  | [MMGE-019] furniture is indicative and selection will be dependent on patient/visitor cohort and service requirements
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | [ITBU-011]
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010] feather edge vinyl or aluminum skirting acceptable if carpet tiles are provided
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] carpet tiles are also acceptable
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 3 |  | [ITCL-006] optional, dependent on patient cohort, provide in areas requiring high staff observation; with indicator button and light
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] with indicator button and light
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] with indicator button and light
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 3 |  | [ITCL-028] optional, dependent on patient cohort, provide in areas requiring high staff observation; with indicator button and light
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] to television, MATV outlet may also be provided depending on local ICT policies
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | SER | ELGP-201 | GPO: double, wall mounted | 3 | 1 |  | [ELGP-208] 1 to television, 2 to room
LNGE-10 | Lounge - Patient / Visitor, 10m2 | Clinical Support Set 2 | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside entry door