## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
MEET-30 | Meeting Room, 30m2 | Administration | Translation and QA Only | 30 | 2700 | MEET-L-30 | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 18 staff seated | The Meeting Room, 30m² provides the space and amenities to accommodate up to 18 staff (seated) for meetings, education and training activities. | ~ The configuration of videoconferencing systems and AV equipment will vary to suit service requirements and local ICT policies. The display system, sound system, microphone, camera, control panels and supporting AV equipment must be carefully considered within the context of the department/facility in order to provide a cohesive, intuitive solution for users. ~ Where a camera is provided for video conferencing the furniture layout should be considered to allow for visibility of users within the field of view. Decor should also be light/neutral and free from busy patterns within the camera view for optimal image quality. ~ Furniture and layout will vary to suit service requirements. Selection of furniture that supports reconfiguration of the layout for flexible use of the space is recommended, e.g. provision of stackable chairs and folding tables. ~ Due to the flexibility of furniture arrangements possible within meeting rooms, the occupancy of the room will vary. The total number of people that may be accommodated in the space will be dependent on the furniture layout. ~ Floor boxes for services may be provided to support flexible use of the space. Location to be confirmed to suit service requirements. ~ The requirement for the inclusion of hearing augmentation systems (e.g. hearing aid induction loops, or solutions that require infrared, radio frequency, or Wi-Fi systems) will be dependent on the specifications/features of the selected ICT/AV equipment and software. Provision of a hearing augmentation system is to be confirmed at project level in consultation with accessibility and ICT experts. ~ Inclusion of a fixed duress button may be considered depending on the location of the room within a department. Fixed duress may not be required where the room is planned in an area that is only accessible by staff. Mobile duress coverage is to be assessed and planned at a department level to suit local security and WHS policies and operational service requirements. ~ Where a meeting room is intended to be used with patients and/or support persons, carers, family, etc., additional features for staff safety (e.g. duress buttons, additional egress doors, etc.) may be required to suit service requirements and local WHS and security policies. An operational model for responding to calls will be needed to support the inclusion of duress call system. ~ When a meeting room is to be used with patients and/or support persons, carers, family, etc. in mental health settings, an alternative egress door should be provided. Where appropriate, equipment may be recessed into walls and finishes, fittings, fixtures and furniture should be suitable for mental health patients. All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. Toughened and laminated glass with a structural interlayer is recommended. Additional requirements for glazing are to be confirmed at project level to suit the specific mental health environment (i.e. non-acute, acute, intensive care). ~ Room booking panels may be provided to suit the department/facility approach to room scheduling. ~ Acoustics are to be carefully considered to ensure appropriate sound levels and to reduce noise transfer to/from adjacent areas for privacy and to reduce disruption, particularly where videoconferencing equipment is provided. Background noise (e.g. from air conditioning) should be minimised. Some hard surfaces may be covered with appropriate acoustic finishes to reduce reverberation as required. ~ Ready access to a telephone in an adjacent space may be required for staff to answer pagers. ~ Access to natural light is desirable and, where overall department planning allows, an external window should be provided. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
MEET-30 | Meeting Room, 30m2 | Administration | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to corridor side, extent dependent on equipment movement in adjacent area
MEET-30 | Meeting Room, 30m2 | Administration | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to room side
MEET-30 | Meeting Room, 30m2 | Administration | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
MEET-30 | Meeting Room, 30m2 | Administration | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
MEET-30 | Meeting Room, 30m2 | Administration | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
MEET-30 | Meeting Room, 30m2 | Administration | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005] may be lockable
MEET-30 | Meeting Room, 30m2 | Administration | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110] as required for distribution across the unit in accordance with AS/NZS 3003
MEET-30 | Meeting Room, 30m2 | Administration | SER | ELGP-126 | GPO: single, in floor box | 4 | 1 |  | [ELGP-103]
MEET-30 | Meeting Room, 30m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 3 | 1 |  | [ELGP-208] to AV/videoconferencing equipment; quantity to be confirmed to suit equipment selection and service requirements
MEET-30 | Meeting Room, 30m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
MEET-30 | Meeting Room, 30m2 | Administration | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
MEET-30 | Meeting Room, 30m2 | Administration | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
MEET-30 | Meeting Room, 30m2 | Administration | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006] configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-30 | Meeting Room, 30m2 | Administration | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1 | [FLCP-006]
MEET-30 | Meeting Room, 30m2 | Administration | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 5 | 1 | Floor Skirting | [FLSK-009] aluminum skirting is also acceptable
MEET-30 | Meeting Room, 30m2 | Administration | FFE | FQBS-142 | CHAIR: meeting room, stackable | 18 | 1 |  | [FQBS-059]
MEET-30 | Meeting Room, 30m2 | Administration | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
MEET-30 | Meeting Room, 30m2 | Administration | FFE | FQTA-126.04 | TABLE: rectangular, 750H, 1500L x 900W, folding, on casters | 3 | 1 |  | [FQTA-086] 2 with services boxes to connect to floor boxes
MEET-30 | Meeting Room, 30m2 | Administration | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
MEET-30 | Meeting Room, 30m2 | Administration | FFE | ITAV-102 | CONTROL PANEL: AV system, wall mounted | 1 | 1 |  | [ITAV-006] configuration of ICT/AV equipment to suit service requirements and local ICT policies; item may be wall mounted, table mounted or portable
MEET-30 | Meeting Room, 30m2 | Administration | FFE | ITAV-111 | COMPUTER: AV system, central processing unit (CPU) | 1 | 1 |  | [ITAV-063] configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-30 | Meeting Room, 30m2 | Administration | FFE | ITAV-121 | DISPLAY SCREEN: AV system | 1 | 1 |  | [ITAV-051] configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-30 | Meeting Room, 30m2 | Administration | FFE | ITAV-132 | CAMERA: AV system, video conferencing, wall mounted | 1 | 1 |  | [ITNE-004] multidirectional, configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-30 | Meeting Room, 30m2 | Administration | FFE | ITAV-142 | MICROPHONE: AV system, ceiling mounted, array | 1 | 1 |  | [ITAV-071] may be recessed in ceiling, configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-30 | Meeting Room, 30m2 | Administration | FFE | ITAV-152 | SPEAKER: AV system, ceiling recessed | 4 | 1 |  | [ITAV-057] configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-30 | Meeting Room, 30m2 | Administration | FFE | ITBU-031 | CONTROL PANEL: room booking system | 1 | 3 |  | [ITAV-062] optional, provision to suit service requirements and local ICT policies
MEET-30 | Meeting Room, 30m2 | Administration | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to AV system control panel
MEET-30 | Meeting Room, 30m2 | Administration | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | [ITIN-016] optional, to room booking control panel if provided
MEET-30 | Meeting Room, 30m2 | Administration | SER | ITIN-021 | OUTLET: data, double RJ45, ceiling mounted | 1 | 1 |  | [ITIN-021] to microphone array
MEET-30 | Meeting Room, 30m2 | Administration | SER | ITIN-022 | OUTLET: data, double RJ45, in floor box | 2 | 1 |  | [ITIN-022]
MEET-30 | Meeting Room, 30m2 | Administration | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
MEET-30 | Meeting Room, 30m2 | Administration | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 2 | 1 |  | [ITIN-036] to AV/videoconferencing equipment; AV outlet type and quantity to be confirmed to suit equipment selection and service requirements
MEET-30 | Meeting Room, 30m2 | Administration | SER | ITIN-162 | FLOOR BOX: power and data outlets, flush floor mounted | 2 | 1 |  | [ITIN-143]
MEET-30 | Meeting Room, 30m2 | Administration | SER | ITIN-172 | DESK BOX: power and data outlets, softwired, flush mounted | 2 | 1 |  | [ITIN-145] softwired for connection to floor box or wall mounted services
MEET-30 | Meeting Room, 30m2 | Administration | FFE | JOBE-001 | BENCH: 450D, laminate | 1 | 1 |  | [FIJO-011]
MEET-30 | Meeting Room, 30m2 | Administration | FFE | JOBE-211 | BENCH SUPPORT: bracket | 2 | 1 |  | [FIHR-065]
MEET-30 | Meeting Room, 30m2 | Administration | FFE | JOBE-251 | CAP: cable access | 1 | 1 |  | [FIJO-099]
MEET-30 | Meeting Room, 30m2 | Administration | D+W | WIFX-156.01 | WINDOW: fixed, external, double glazed, sill at 750H | 1 | 1 | External - Window 1 | [DWWH-005] access to natural light is desirable
MEET-30 | Meeting Room, 30m2 | Administration | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 2 | [WLWA-004]
MEET-30 | Meeting Room, 30m2 | Administration | FIN | WLFI-202 | ACOUSTIC TREATMENT: wall panel, prefinished | 12 | 3 | Wall Finish 1 | [WLWA-001] optional; to suit acoustic requirements