## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
MEET-55 | Meeting Room, 55m2 | Administration | Translation and QA Only | 55 | 2700 | MEET-L-55 | 3 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | up to 45 staff seated | A large multipurpose room for staff meetings, education and training activities. Requirement for Hearing Augmentation to be confirmed. | ~ An operable wall may be provided to open this room to an adjoining meeting room, increasing capacity for lectures, training activities or events. Connections and coordination between AV and video conferencing equipment in adjoining rooms will need to be considered to support both separate and combined activities. ~ Video conferencing systems and AV equipment will be dependent on service requirements and local ICT policies. The lectern design, display system, sound system, microphone, room and video conferencing control and supporting AV equipment must be carefully considered to provide a cohesive solution for users. ~ To support video conferencing, decor should be light/neutral and free from busy patterns within the camera view for optimal image quality. ~ Room booking panels may be provided to suit service/facility approach to room scheduling. ~ Occupancy will vary, with the total number of people that may be accommodated in the space dependent on furniture layout. ~ Furniture and layout will vary to suit service requirements. Furniture considerations include provision of chairs with integral note tables, stackable chairs and folding tables to support reconfiguration of the layout for flexible use of the space. ~ A storage zone or enclosed storeroom may be provided to hold additional furniture to support alternate layouts. If multiple rooms are provided, furniture storage areas may be shared. ~ Floor boxes for services may be provided to support flexible use of the space. Location to be confirmed to suit service requirements. ~ Acoustics to be carefully considered to ensure appropriate sound levels, particularly with video conferencing equipment provided, and to reduce noise transfer to/from adjacent areas for privacy and to reduce disruption. Background noise (e.g. from air conditioning) should be minimised. Hard surfaces may be covered to reduce reverberation as required. ~ Where a meeting room is intended to be used with patients and/or family, additional features for staff safety (e.g. duress buttons, additional egress doors, etc.) may be considered to suit service requirements. An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ When used with patients and/or family in mental health settings, an alternative egress door should be provided. Where possible, equipment should be recessed into walls and finishes, fittings, fixtures and furniture should be suitable for mental health patients. All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288. ~ Ready access to a telephone in an adjacent space may be required to answer pagers. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
MEET-55 | Meeting Room, 55m2 | Administration | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 2 | 1 | Internal - Door 1 | [DWPR-001] to room side
MEET-55 | Meeting Room, 55m2 | Administration | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 1 | [DWPR-001] to corridor side, extent dependent on equipment movement in adjacent area
MEET-55 | Meeting Room, 55m2 | Administration | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
MEET-55 | Meeting Room, 55m2 | Administration | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
MEET-55 | Meeting Room, 55m2 | Administration | D+W | DOHI-212.01 | DOOR: hinged, 2 leaves, 1600 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-052] may be lockable
MEET-55 | Meeting Room, 55m2 | Administration | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110] as required for distribution across the unit in accordance with AS/NZS 3003
MEET-55 | Meeting Room, 55m2 | Administration | SER | ELGP-126 | GPO: single, in floor box | 4 | 1 |  | [ELGP-103] to floor box for lectern
MEET-55 | Meeting Room, 55m2 | Administration | SER | ELGP-126 | GPO: single, in floor box | 8 | 3 |  | [ELGP-103] optional, 4 to each floor box if provided
MEET-55 | Meeting Room, 55m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 3 | 1 |  | [ELGP-208] to AV/videoconferencing equipment; quantity to be confirmed to suit equipment selection and service requirements
MEET-55 | Meeting Room, 55m2 | Administration | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
MEET-55 | Meeting Room, 55m2 | Administration | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
MEET-55 | Meeting Room, 55m2 | Administration | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
MEET-55 | Meeting Room, 55m2 | Administration | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006] configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-55 | Meeting Room, 55m2 | Administration | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1 | [FLCP-006]
MEET-55 | Meeting Room, 55m2 | Administration | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 5 | 1 | Floor Skirting | [FLSK-009] aluminum skirting is also acceptable
MEET-55 | Meeting Room, 55m2 | Administration | FFE | FQBS-142 | CHAIR: meeting room, stackable | 42 | 1 |  | [FQBS-059]
MEET-55 | Meeting Room, 55m2 | Administration | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
MEET-55 | Meeting Room, 55m2 | Administration | FFE | FQTA-124.04 | TABLE: rectangular, 750H, 1200L x 900W, folding, on casters | 4 | 1 |  | [FQTA-086] quantity, type and size to be confirmed to suit service requirements
MEET-55 | Meeting Room, 55m2 | Administration | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
MEET-55 | Meeting Room, 55m2 | Administration | FFE | ITAV-102 | CONTROL PANEL: AV system, wall mounted | 1 | 1 |  | [ITAV-006] configuration of ICT/AV equipment to suit service requirements and local ICT policies; item may be wall mounted or portable
MEET-55 | Meeting Room, 55m2 | Administration | FFE | ITAV-111 | COMPUTER: AV system, central processing unit (CPU) | 1 | 1 |  | [ITAV-063] configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-55 | Meeting Room, 55m2 | Administration | FFE | ITAV-121 | DISPLAY SCREEN: AV system | 1 | 1 |  | [ITAV-051] configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-55 | Meeting Room, 55m2 | Administration | FFE | ITAV-131 | CAMERA: AV system, video conferencing, ceiling mounted | 1 | 3 |  | [ITAV-064] optional, multidirectional, to rear of room for view of speaker, configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-55 | Meeting Room, 55m2 | Administration | FFE | ITAV-132 | CAMERA: AV system, video conferencing, wall mounted | 1 | 1 |  | [ITNE-004]
MEET-55 | Meeting Room, 55m2 | Administration | FFE | ITAV-142 | MICROPHONE: AV system, ceiling mounted, array | 2 | 1 |  | [ITAV-071] may be recessed in ceiling, configuration of ICT/AV equipment to suit service requirements and local ICT policies
MEET-55 | Meeting Room, 55m2 | Administration | FFE | ITAV-152 | SPEAKER: AV system, ceiling recessed | 6 | 1 |  | [ITAV-057]
MEET-55 | Meeting Room, 55m2 | Administration | FFE | ITAV-191 | LECTERN: mobile, with microphone | 1 | 1 |  | [FQDW-006 and ITAV-014]
MEET-55 | Meeting Room, 55m2 | Administration | FFE | ITBU-031 | CONTROL PANEL: room booking system | 1 | 3 |  | [ITAV-062] optional, provision to suit service requirements and local ICT policies
MEET-55 | Meeting Room, 55m2 | Administration | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | 3 |  | [ITIN-011] optional, to speaker camera at rear of room if provided
MEET-55 | Meeting Room, 55m2 | Administration | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 3 |  | [ITIN-016] optional, to room booking control panel if provided
MEET-55 | Meeting Room, 55m2 | Administration | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | 1 |  | [ITIN-016] to AV system control panel
MEET-55 | Meeting Room, 55m2 | Administration | SER | ITIN-021 | OUTLET: data, double RJ45, ceiling mounted | 2 | 1 |  | [ITIN-021] to microphone array
MEET-55 | Meeting Room, 55m2 | Administration | SER | ITIN-022 | OUTLET: data, double RJ45, in floor box | 2 | 3 |  | [ITIN-022] optional, 1 to each floor box if provided
MEET-55 | Meeting Room, 55m2 | Administration | SER | ITIN-022 | OUTLET: data, double RJ45, in floor box | 1 | 1 |  | [ITIN-022] to floor box for lectern
MEET-55 | Meeting Room, 55m2 | Administration | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 2 | 1 |  | [ITIN-036] to AV/videoconferencing equipment; AV outlet type and quantity to be confirmed to suit equipment selection and service requirements
MEET-55 | Meeting Room, 55m2 | Administration | SER | ITIN-162 | FLOOR BOX: power and data outlets, flush floor mounted | 2 | 3 |  | [ITIN-143] optional, to support flexible layout, location to be confirmed to suit service requirements
MEET-55 | Meeting Room, 55m2 | Administration | SER | ITIN-162 | FLOOR BOX: power and data outlets, flush floor mounted | 1 | 1 |  | [ITIN-143] to lectern
MEET-55 | Meeting Room, 55m2 | Administration | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 2 | [WLWA-004]
MEET-55 | Meeting Room, 55m2 | Administration | FIN | WLFI-202 | ACOUSTIC TREATMENT: wall panel, prefinished | 12 | 3 | Wall Finish 1 | [WLWA-001] optional; to suit acoustic requirements