## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
MEET-L-20 | Meeting Room / Tutorial Facility | 20 |  | Up to 16 | Available 24 Hours | Sound attenuation level high, Acoustic privacy is required. | A multipurpose room for staff meetings, teaching, training/education and patient group activities. This room may also accommodate other meetings such as those held with the visiting Magistrate Review Hearings in Mental Health units. Refer to AusHFG mental health HPUs for specific requirements. Seek audiovisual expertise for complex, project specific requirements. An external outlook is desirable. A second egress door may be required for staff safety and security. A specific requirement for Magistrate Review Hearings. The room may be located in close proximity to a Beverage Bay as required. Acoustics: sound attenuation level - high. Acoustic privacy essential. Size of space and FF&E quantity/type to be adapted to suit specific project briefing requirements as per AusHFG HPUs. Add 1.2m2 per additional person and allow 1.5m2 for wheelchair parking space as required.

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
MEET-L-20 | Meeting Room / Tutorial Facility | Fabrics | 1130 | Floor finish | 1 | Slip resistant vinyl also acceptable. | Carpet | 90/10 Wool/ Nylon | Carpet tiles | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | Fabrics | 2010 | Skirting | 1 |  | Vinyl | Prefinished | Feather edged, 150 mmH | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | Fabrics | 2706 | Observation | 1 | Optional | Alum/ Glass | Powdercoat | Internal window with internal blinds | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | Fabrics | 5060 | Ceiling - Acoustic | 1 |  | Acoustic | Prefinished | Drop-in tiles, 600x1200 | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | Fabrics | 7001 | Windows | 1 | desirable |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | Fabrics | 8010 | Door protection | 1 |  | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | Fabrics | 8040 | Door protection | 1 | Optional. To be decided at project level. | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | Fabrics | 9001 | Door - 1100mm | 1 | Egress door, may also be required for magistrate's use in Mental Health units, optional. | Solid Core | Paint | Single leaf | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | Fabrics | 9004 | Door - 1100mm | 1 | 910mm clear opening, lock set | Solid Core/ Glass | Paint | Single leaf, observation panel | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | FE | FE-11100 | Computer - laptop | 1 | Not fixed or desktop computer, optional. Refer project specific operational policies for secure storage when not in use. |  |  |  | Yes | Yes | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | FE | FE-6466 | Telephone - teleconference | 1 | Optional. |  |  |  | Yes | Yes | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | FE | FE-7718 | Microphone - video-conferencing | 1 | Optional. For Magistrate Hearings and integral with video-conferencing system. Requirement to be confirmed at project level. Ceiling or table mounted. |  |  |  | Yes | Yes | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | FE | FE-7719 | Monitor - LCD | 1 | Image projection. Number and size of monitor/s to suit project specific requirements. Video-conferencing for Magistrate Hearings optional, to be confirmed at project level. Provide conduit for wiring from monitors to services floor box. |  |  |  | Yes | Yes | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | FE | FE-7720 | Speakers - video-conferencing, wall mounted | 2 | Optional. For Magistrate Hearings and integral with video-conferencing system. Requirement to be confirmed at project level. |  |  |  | Yes | Yes | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | FE | FE-7721 | Video-conferencing system | 1 | Optional, for Mental Health Review Hearings. Console, integral with camera, monitor, speakers and microphone. Configuration and Mental Health Review Board requirement to be confirmed at project level. |  |  |  | Yes | Yes | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | FE | FE-7722 | Camera - video-conferencing | 1 | Optional. For Magistrate Hearings. Requirement to be confirmed at project level. |  |  |  | Yes | Yes | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | FF | FF-1050 | Bench - laminate | 1 | Optional. Length to suit layout, refer RLS or project specific requirements. |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | FF | FF-17360 | Pinboard - fabric covered | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | FF | FF-2060 | Chair - meeting room | 16 | May be stackable. Heavy duty for Review Hearings. |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | FF | FF-23040 | Table - meeting | 4 | Smaller tables may be located together. Folding or general use, heavy duty for Review Hearings. |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | FF | FF-24405 | Whiteboard - magnetic | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | FF | FF-3350 | Clock - battery operated | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | FF | FF-4420 | Cupboard - under bench, lockable | 1 | adjustable shelf, optional. Number to suit layout, refer RLS or project specific requirements. Storage solution for consumables and equipment to meet project specific Infection Control and OHS requirements. |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | FF | FF-5824 | Waste bin - general | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | FF | FF-5828 | External window dressing | 1 | Number to align with window configuration, if provided. Window dressing type to comply with Infection Control policy. Blackout may be required for audiovisual presentations and video-conferencing, if required. |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | FF | FF-7513 | Bracket LCD monitor | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | FF | FF-7514 | AV rack | 1 | Optional. May be required for Magistrate Hearings. Integral with video-conferencing system. Requirement to be confirmed at project level. |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | SE | S-10005 | Duress alarm | 1 | Optional. Two (2) fixed buttons are required for Review Hearings in Mental Health units. Refer to AusHFG specific mental health HPU requirements. Will not be required in staff areas. |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | SE | S-1006 | Voice / Data outlet: double | 1 | floor services box |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | SE | S-1006 | Voice / Data outlet: double | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | SE | S-1007 | Voice / Data outlet: triple | 1 | Optional, on wall for video-conferencing unit (minimum requirement for VC is 1-triple outlet) |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | SE | S-1090 | TV: MATV | 1 | Optional. May be replaced with data outlet, in accordance with ICT policy. May be required for educational purposes, to be determined at project level. If required add television, bracket and dedicated power. |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | SE | S-1387 | Floor services box: flush mount | 1 | Data and power outlets. Verify location before installation. |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | SE | S-2088 | Light switch: single | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | SE | S-6000 | General fluorescent | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | SE | S-6110 | Downlights: dimmable | 1 | For audiovisual presentations, optional. |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | SE | S-8080 | Emergency call | 1 | + indicator button & light, optional. For patient group/education purposes only. Will not be required in staff areas. |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | SE | S-9001 | GPO: Double | 2 | floor services box |  |  |  | No | No | No | No | No | No | No | No | No
MEET-L-20 | Meeting Room / Tutorial Facility | SE | S-9001 | GPO: Double | 5 | 1 above bench if provided |  |  |  | No | No | No | No | No | No | No | No | No