## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
MEET-L-55 | Meeting Room, 55m2 | 55 | Available up to 24 Hours |  |  | Sound attenuation level high, Acoustic privacy is required. | The large Meeting Room will provide videoconferencing facilities for staff and client meetings. It is a multipurpose room also used for training or educational purposes. The room should be located away from high traffic and noise areas. An operable wall will allow the room to be sub-divided, so that two separate meetings can be run simultaneously. For use in mental health applications, an alternative egress door should be provided and equipment recessed into walls where possible; finishes, fittings & fixtures and furniture should be suitable for mental health patients. For Mental Health rooms, all glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288, specifically, toughened laminated glass with a standard nominal thickness of 10.38mm, or equivalent approved. Integration of Video-conference equipment should be considered including the following: Lectern design, Room and VC Control (AMX, Creston, Joey etc.), Room sound system, Room microphone system (dual, wireless, ceiling or combination) , Display system (e.g. projector, monitor or monitors), AV equipment (matrix switch, amp, secondary camera etc.) Discussions within the room should not be heard in adjacent rooms or corridor; reverberation time RT60 in the room ideally less than 250ms; background noise (from HVAC or other sources) should be kept to a minimum, below 40dBA; avoid parallel hard surfaces in the room; acoustic panelling may be considered. Additional design requirements: - table should be positioned so that all chairs face the camera; tables may be small modular type located together or oval - high level of lighting is required in the room to illuminate faces in view of the camera; avoid bright spots, shadows or dark patches; the front light fittings should be 45 degrees above the subject's horizontal sightline; track lighting with halogen lamps may be considered - room decor should avoid white or pastel colours for optimal picture quality; soft furnishings should avoid busy patterns in camera view - hard surfaces should be covered to minimise echo. Provide data and ISDN (Onramp2) connections and 2 DGPOs for the videoconferencing unit in addition to other power/data provisions in the room; verify locations on site - Network termination boxes (NT1), if required for local areas, should be located within the room; if adjacent rooms are sharing lines, no patch panels should be used, outlets (sBus) should be parallel & active.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
MEET-L-55 | Meeting Room, 55m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1 |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | Lockable, wth cover to observation panel | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FA | DWPR-003 | DOOR PROTECTION: kickplate, to 300 AFFL, vinyl, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | Egress door, may also be required for magistrate's use in Mental Health options | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | DWWD-014 | WINDOW DRESSING: external window, blackout | 1 | optional; or black-out blinds for audiovisual presentations | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FA | DWWH-005 | WINDOW | 1 | not essential; if provided, preferably not on a wall in front of the camera | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | ELBO-015 | SWITCH: light, single | 4 |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | in ceiling for data projector; optional | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | as required | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | ELGP-203 | GPO: double, in floorbox | 4 | optional, 2 in each floorbox | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | ELGP-208 | GPO: double, wall mounted | 1 | videoconferencing unit; verify location before installation | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | ELGP-208 | GPO: double, wall mounted | 5 | on walls; 3-VC unit; 2 may be provided on wall or in floor services box as required | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 1 | videoconferencing unit; verify location before installation | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | FIBM-013 | NOTICEBOARD: fixed, fabric covered | 2 |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 2 |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 2 |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 2 |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | FIJO-117 | CUPBOARD: tall, double door, adj shelves, lockable | 2 |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | FIJO-117 | CUPBOARD: tall, double door, adj shelves, lockable | 1 | for video-conferencing equipment; optional | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 2 |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | FIJO-140 | CUPBOARD: underbench, single door, adj shelves | 2 |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | FIJO-208 | CUPBOARD: wall mount, shelf unit, fixed shelves, for av equipment | 2 | for videoconferencing unit | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FA | FLCP-003 | FLOOR FINISH: carpet, broadloom, 48 oz., 90/10 wool/nylon | 1 |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | FQBS-017 | CHAIR: meeting room | 44 | some with arms | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 2 |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | FQDW-006 | LECTERN: mobile | 1 |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | FQGE-005 | CLOCK: analogue, battery operated | 2 |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | FQGE-069 | SCREEN: projection, ceiling mounted, automatic | 1 | optional | Yes | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | ITAV-009 | MICROPHONE | 2 | videoconference unit component; will requrie a min of 2 for 35m2 room - may require 1 microphone between every 2 chairs; on table; may also be ceiling mounted | Yes | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | ITAV-022 | PROJECTOR: data, ceiling mounted | 1 | optional | Yes | Yes | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | ITAV-051 | DISPLAY SCREEN: audio visual | 2 | videoconference unit component; Plasma, 50" min, high resolution screen with HDMI (High Definition Multimedia Interface); 2nd screen optional | Yes | Yes | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 2 |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 1 | in ceiling for data projector; optional | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | ITIN-022 | OUTLET: data, double RJ45, in floorbox | 1 | optional, 1 in each floorbox | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 3 | on wall for VC unit (min requirement for VC is 1-triple outlet); 1 outlet for IP connectivity for videoconferencing unit; ISDN (Onramp2) connection, ISDN NT box only if required; network terminator boxes (NT1) to be located within the room; equipment to be directly connected, no patch panels; verify location before installation | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | ITIN-070 | OUTLET: MATV | 2 | 1 to each display screen | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | ITIN-143 | FLOORBOX: for power, data, AV, flush mounted | 2 | for data and power, optional; verify location before installation | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | ITNE-004 | CAMERA: video conferencing | 1 | 2nd camera optional; for video stream switching | Yes | Yes | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | ITNE-004 | CAMERA: video conferencing | 1 | part of videoconferencing unit; mounted to monitor/s or wall mounted | Yes | Yes | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | ITNE-010 | COMPUTER: laptop or other mobile device | 2 | for presentations; optional | Yes | Yes | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | ITNE-013 | CONTROL UNIT: video conferencing | 2 |  | Yes | Yes | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | ITNE-042 | SPEAKER: video conferencing, wall mount | 2 |  | Yes | Yes | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 2 | 1 wall phone outside room entry | No | Yes | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | ITNE-060 | TELEPHONE: teleconferencing module | 2 |  | Yes | Yes | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | SE | ITSE-006 | BUTTON: duress, fixed | 2 | optional. Refer HPU requirements. Will not be required in staff-only areas. | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FFE | WLPT-011 | WALL: operable | 1 |  | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FA | WLWA-001 | WALL FINISH: acoustic panels, prefinished | 1 | may be required depending on room acoustics | No | No | No | No | No | No | No | No | No
MEET-L-55 | Meeting Room, 55m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 | Decor to be light/neutral, avoid white and pastel colours, free from patterning, no grey/ bue-grey shades for optimal picture quality | No | No | No | No | No | No | No | No | No