## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | Translation and QA Only | 30 | 3000 |  | 4 | 07.04.2026 |  | 8am to 5pm, daily (may vary depending on services requirements) | up to 4 staff | The Mortuary - Autopsy Room is for undertaking post mortem examinations. An observation area is to be provided to at least one Autopsy Room within a department. | ~ Layout of tables and orientation of observation bay may be adjusted to suit the type of autopsy being performed (e.g. coronial or non-coronial). The Mortuary - Autopsy Room should be located with ready access to Mortuary - Body Holding. ~ doors to be sealed for odours, post mortem table to have water flushing system. Appropriate Smoke/Heat detection to be considered. | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to room side
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 2 | [DWGL-005] to anteroom; door seals required
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-033] to corridor; door seals required
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | D+W | WIFX-008.01 | WINDOW: fixed, internal, single glazed, sill at 1050H | 1 | 1 | Internal - Window 1 | [DWOB-005] to observation area if provided
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | [FIBM-019] optional
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 2 | 1 |  | [FIDI-031] to basin
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FIHR-029 | HOOK: equipment, wall mounted | 1 | 3 |  | [FIHR-029] optional, for lifter straps/slings
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 2 | 1 |  | [FIHR-016]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | [FIHR-067]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FIRT-101 | GRAB RAIL: straight, horizontal | 2 | 1 |  | [FIRT-005] to boot wash
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FIRT-116 | GRAB RAIL: U-shaped, floor mounted | 1 | 1 |  | [FIRT-046] to boot wash
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 3 |  | [FQBS-051] optional, dependent on project requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | [MMGE-048]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FQGE-121 | CLOCK: analogue display, battery operated | 1 | 1 |  | [FQGE-005]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-043]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FQWS-057 | BIN: general waste, 120L | 1 | 1 |  | [FQCW-015]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | FQWS-237 | BIN: clinical waste, 120L | 1 | 1 |  | [FQCW-004]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1 |  | [HYBA-009]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | HYBA-301 | SINK: single bowl | 1 | 1 |  | [HYBA-055]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | HYGE-031 | TROUGH: boot wash, floor recessed | 1 | 1 |  | [HYGE-026]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | HYGE-151 | HOSE REEL: retractable | 1 | 1 |  | [HYTP-003]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | HYSH-111 | STATION: emergency, safety, shower and eye wash, wall mounted | 1 | 1 |  | [HYTP-023]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | HYTP-062 | TAPWARE: basin, tap set, fixture mounted, lever handles | 2 | 1 |  | [HYTP-038]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | HYTP-176 | TAPWARE: sink, tap set, fixture mounted, laboratory | 1 | 1 |  | [HYTP-034] to dissection table
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | HYTP-406 | TAPWARE: spout, wall mounted | 1 | 1 |  | [HYTP-028] to boot wash
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | HYTP-416 | TAPWARE: tap, wall mounted | 1 | 1 |  | [HYTP-030] to boot wash
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | HYTP-421 | TAPWARE: hosecock, wall mounted | 1 | 1 |  | [HYTP-012] to hose reel
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053] suitable for use in wet zone
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | ITNE-121 | COMPUTER: single display screen, all-in-one | 1 | 1 |  | [ITNE-066] suitable for use in wet zone
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1 |  | [ITNE-067] suitable for use in wet zone
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | JOBE-033 | BENCH: 600D, stainless steel lipped | 1 | 1 |  | [FIJO-021] with wet edge and integral sink
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | JOBE-231 | BENCH SUPPORT: legs and frame, stainless steel | 1 | 1 |  | [FIJO-100]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | LIFX-131 | LIGHT: procedure, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | [LIFX-014] hardwired, a second light may be provided dependent on service requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | MMBE-211 | TRACK: patient lifter, fixed, ceiling mounted | 1 | 1 |  | [MMBE-071] optional, mobile lifter may be used, bariatric capacity to be confirmed based on service requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | MMBE-251 | CASSETTE MOTOR: patient lifter, for ceiling mounted system | 1 | 3 |  | [MMBE-071] optional, mobile lifter may be used, bariatric capacity to be confirmed based on service requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | MMBE-266 | SLING: patient lifter, supine | 1 | 3 |  | [MMBE-071] optional, mobile lifter may be used, bariatric capacity to be confirmed based on service requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | MMGE-201 | SCALES: digital, benchtop | 1 | 1 |  | [MMGE-185]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | MMMT-001 | TABLE: evisceration, autopsy, fixed, height adjustable | 1 | 3 |  | [MMLA-086] bariatric capacity to be determined based on service requirements, services on table to be considered: suction capabilities (built-in or provided), power to table, power outlets (if not on table), down draft (optional, built-in to table), water connection (built-in to table)
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | MMMT-006 | TABLE: dissection, fixed, height adjustable | 1 | 1 |  | [MMLA-087] with integral sink
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FFE | MMTR-071 | TROLLEY: equipment, 490W x 490D x 900H nom | 2 | 1 |  | [MMGE-119]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 10 | 1 | Floor Skirting | [FLSK-010]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FIN | FLVY-112 | FLOOR FINISH: vinyl, seamless, non-slip, safety | 1 | 1 | Floor Finish 1 | [FLVY-004] junction with evisceration table to be considered to prevent water ingress
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | FIN | WLFI-011.06 | WALL FINISH: vinyl, to 2100 AFFL | 8 | 1 | Wall Finish 2 | [WLWA-023]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123] to computer. IP rated to suit AS/NZS wet zone requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | ELGP-191 | GPO: single, special, for equipment, wall mounted | 2 | 1 |  | [ELGP-106] power to evisceration and dissection tables (if not part of table configuration). Required to be emergency power/generator backed. IP rated to suit AS/NZS wet zone requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | ELGP-191 | GPO: single, special, for equipment, wall mounted | 8 | 1 |  | [ELGP-106] 4x outlets on evisceration and dissection tables, dependent on service requirements and vendor specifications. Required to be emergency power/generator backed. IP rated to suit AS/NZS wet zone requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | [ELGP-223] IP rated to suit AS/NZS wet zone requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-015] 1x general room lights, 1x task light over dissection bench. IP rated to suit AS/NZS wet zone requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004] to boot wash
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | HYDR-025 | DRAIN: floor waste, linear | 2 | 1 |  | [HYDR-003]
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | HYDR-211 | DIRECT CONNECTION: wastewater, evisceration/autopsy table | 2 | 1 |  | [HYDR-001] 1 to autopsy table, 1 to evisceration table; confirm requirements at project level
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | [HYTP-008] connection only, to evisceration and dissection tables, dependent on service requirements and vendor specifications
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 2 | 1 |  | 1 to sink, 1 to basin
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | 1 to hosecock, 1 to boot trough tapware
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 2 | 1 |  | [HYTP-013] connection only, to evisceration and dissection tables, dependent on service requirements and vendor specifications
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | HYTP-452 | DIRECT CONNECTION: water, hot | 1 | 1 |  | to sink
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3 | 1 |  | [ITIN-016] IP rated to suit AS/NZS wet zone requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] IP rated to suit AS/NZS wet zone requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | [ITSE-029] suitable for use in wet zone
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | LIFX-101 | LIGHT: task, ceiling recessed | 1 | 1 |  | [LIFX-037] task lighting over dissection table, articulated task light is also acceptable dependent on service requirements
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | MEEX-122 | DIRECT CONNECTION: exhaust, downdraft | 1 | 3 |  | [MEEX-017] optional, on evisceration and dissection tables, dependent on service requirements and vendor specifications
MOR-AU | Mortuary - Autopsy Room | Mortuary and Autopsy | SER | MGAS-063 | OUTLET: suction, wall mounted | 2 | 1 |  | [MGAS-060] on evisceration and dissection tables, dependent on service requirements and vendor specifications