## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | Translation and QA Only | 15 | 2700 |  | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 4 workstations;;; | An Office - Clinical Workroom, typically adjoining or in close proximity to a Staff Station, is for staff to write up notes, review patient records and digital images, hold confidential discussions, store records and conduct handovers. | ~ One computer has been shown as a downtime computer with UPS power; this requirement will need to be confirmed by the department. The downtime computer, if required by a department, may alternatively be provided in a Staff Station. Provision of a downtime computer will need to be rationalised across the unit to avoid duplication. ~ Location of power and data outlets (above or below the bench) is to meet local operational/WHS requirements. Cable management solutions to be considered to meet infection control and cleaning requirements. ~ A desktop printer may be provided. Printing/scanning/photocopying facilities should be consolidated across the unit to suit service requirements. ~ Provision of height adjustable workstations may be considered depending on local policies and staff accessibility requirements. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | D+W | DOHI-013.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | [DWGL-005]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | D+W | WIFX-007.01 | WINDOW: fixed, internal, single glazed, sill at 900H | 1 | 3 | Internal - Window 1 | [DWOB-002] optional
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 1 |  | [FIBM-019]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 3 |  | [FIBM-019] optional, above bench
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | FIHR-322 | BRACKET: keyboard and mouse, fixed height, wall mounted | 1 | 1 |  | [FIHR-093] to patient flow monitor
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | FIHR-331 | BRACKET: display screen, single, fixed, wall mounted | 1 | 1 |  | [FIHR-006] to patient flow monitor
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | FQBS-171 | CHAIR: office, ergonomic | 4 | 1 |  | [FQBS-018]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | ITCL-331 | DISPLAY SCREEN: patient flow system | 1 | 1 |  | [ITBU-013]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | ITNE-071 | TELEPHONE: handset, desktop | 4 | 1 |  | [ITNE-049]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 4 | 1 |  | [ITNE-007]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | ITNE-201 | INPUT DEVICE: keyboard and mouse | 1 | 1 |  | [ITNE-067] to patient flow monitor
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | ITNE-311 | PRINTER: desktop | 1 | 1 |  | [ITNE-023]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | ITSE-071 | CHARGER: security, duress, wireless devices, wall mounted | 2 | 3 |  | [ITCL-037] optional
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | JOBE-061 | BENCH: 750D, laminate | 1 | 1 |  | [FIJO-031]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | JOBE-211 | BENCH SUPPORT: bracket | 3 | 1 |  | [FIHR-080] legs are also acceptable, quantity to be confirmed to achieve required support, ensure location does not impact leg clearance at workstations
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | JOBE-251 | CAP: cable access | 4 | 1 |  | [FIJO-099]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead is also acceptable
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 6 | 1 |  | [FIJO-152] overhead joinery may be configured to include pigeon holes for record storage as required
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] carpet tiles are also acceptable
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | SER | ELGP-161 | GPO: single, UPS, wall mounted | 1 | 1 |  | [ELGP-130] to printer; UPS to be provided if downtime computer required
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | SER | ELGP-261 | GPO: double, UPS, wall mounted | 2 | 1 |  | [ELGP-235] UPS to be provided if downtime computer required. location of outlets to meet local operational/WHS requirements
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-015] 1 x general room lighting, 1 x task light
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 1 |  | [ITIN-016] 1 x to patient flow monitor, 1 x to printer
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | SER | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 4 | 1 |  | [ITIN-036] location of outlets to meet local operational/WHS requirements
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006] below desk, wall mounted is also acceptable
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | SER | LIFX-108 | LIGHT: task, integral to joinery | 6 | 1 |  | [LIFX-008] under wall mounted joinery
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | SER | ELGP-201 | GPO: double, wall mounted | 1 | 3 |  | [ELGP-208] optional, for duress charging station if provided
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | SER | ELGP-201 | GPO: double, wall mounted | 3 | 1 |  | [ELGP-208] for BYO devices, to be located above desk for easy access
OFF-CLN | Office - Clinical Workroom | Clinical Support Set 2 | SER | ELGP-201 | GPO: double, wall mounted | 7 | 1 |  | [ELGP-208] location of outlets to meet local operational/WHS requirements