## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
OVBR | Overnight Stay - Bedroom | Staff Amenities | Translation and QA Only | 10 | 2700 |  | 6 | 07.04.2026 |  | Available 24 hours | 1 staff / visitor | A 1 bed room with an adjoining ensuite for staff, parents or carers needing to remain on close call overnight. | ~ The room shall be lockable. ~ An external outlook is required. ~ Overnight stay bedroom and ensuite layouts may be adjusted to provide accessible facilities i.e. as required if a standalone suite is provided or in a portion of rooms if multiple overnight stay suites are provided. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
OVBR | Overnight Stay - Bedroom | Staff Amenities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 3 | Internal - Door 1 | [DWPR-001] optional
OVBR | Overnight Stay - Bedroom | Staff Amenities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 3 | Internal - Door 2 | [DWPR-001] optional; to bedroom side
OVBR | Overnight Stay - Bedroom | Staff Amenities | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 3 | Internal - Door 2 | [DWPR-001] optional; to ensuite side
OVBR | Overnight Stay - Bedroom | Staff Amenities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
OVBR | Overnight Stay - Bedroom | Staff Amenities | D+W | AHWCV-002 | WINDOW COVERING: blind, roller, double | 1 | 1 | External - Window 1 | [DWWD-004] blackout fabric
OVBR | Overnight Stay - Bedroom | Staff Amenities | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
OVBR | Overnight Stay - Bedroom | Staff Amenities | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
OVBR | Overnight Stay - Bedroom | Staff Amenities | D+W | DOHI-003 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 2 | [DWSC-003] to ensuite; lockable
OVBR | Overnight Stay - Bedroom | Staff Amenities | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-003] to corridor; lockable
OVBR | Overnight Stay - Bedroom | Staff Amenities | SER | ELGP-101 | GPO: single, wall mounted | 1 | 3 |  | [ELGP-109] optional, to fridge if provided
OVBR | Overnight Stay - Bedroom | Staff Amenities | SER | ELGP-201 | GPO: double, wall mounted | 2 | 1 |  | [ELGP-208] 1 to bedside, 1 to desk
OVBR | Overnight Stay - Bedroom | Staff Amenities | SER | ELSW-001 | SWITCH: light | 2 | 1 |  | [ELBO-015] 1 to general room lighting, 1 to reading light
OVBR | Overnight Stay - Bedroom | Staff Amenities | FIN | FLCP-006 | FLOOR FINISH: carpet tiles | 1 | 1 | Floor Finish 1 | [FLCP-006]
OVBR | Overnight Stay - Bedroom | Staff Amenities | FIN | FLSK-026 | SKIRTING: vinyl, feather edge | 8 | 1 | Floor Skirting | [FLSK-009] aluminum or timber skirting is also acceptable
OVBR | Overnight Stay - Bedroom | Staff Amenities | FFE | FQBS-061 | BED: domestic, single | 1 | 1 |  | [FQBS-004]
OVBR | Overnight Stay - Bedroom | Staff Amenities | FFE | FQBS-071 | MATTRESS: domestic, single | 1 | 1 |  | [FQBS-004]
OVBR | Overnight Stay - Bedroom | Staff Amenities | FFE | FQBS-171 | CHAIR: office, ergonomic | 1 | 3 |  | [FQBS-018] optional, to desk if provided
OVBR | Overnight Stay - Bedroom | Staff Amenities | FFE | FQCA-401 | FRIDGE: domestic, 120L nom, single door, under bench | 1 | 3 |  | [FQCA-030] optional, dependent on project requirements
OVBR | Overnight Stay - Bedroom | Staff Amenities | FFE | FQDW-111.01 | WORKSTATION: straight, fixed height, 900H, 600D x 1000W | 1 | 3 |  | [FQDW-053] optional
OVBR | Overnight Stay - Bedroom | Staff Amenities | FFE | FQSN-103 | BEDSIDE TABLE: floor standing, domestic | 1 | 1 |  | [FQTA-001]
OVBR | Overnight Stay - Bedroom | Staff Amenities | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
OVBR | Overnight Stay - Bedroom | Staff Amenities | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] to bedside for phone
OVBR | Overnight Stay - Bedroom | Staff Amenities | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026] optional, to desk if provided
OVBR | Overnight Stay - Bedroom | Staff Amenities | FFE | ITNE-071 | TELEPHONE: handset, desktop | 1 | 1 |  | [ITNE-049] may be wall mounted
OVBR | Overnight Stay - Bedroom | Staff Amenities | D+W | ITSE-261 | READER: security, access control, proximity card, wall mounted | 1 | 3 | Internal - Door 1 | [ITSE-038] optional
OVBR | Overnight Stay - Bedroom | Staff Amenities | FFE | JOCU-413 | WARDROBE: built-in, single door, fixed shelves, clothing rail | 1 | 1 |  | [FIJO-130]
OVBR | Overnight Stay - Bedroom | Staff Amenities | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] to wardrobe; plasterboard bulkhead is also acceptable
OVBR | Overnight Stay - Bedroom | Staff Amenities | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | [LIFX-011]
OVBR | Overnight Stay - Bedroom | Staff Amenities | D+W | WIFX-158.01 | WINDOW: fixed, external, double glazed, sill at 1050H | 1 | 1 | External - Window 1 | [DWWH-005] essential
OVBR | Overnight Stay - Bedroom | Staff Amenities | FIN | WLFI-001 | WALL FINISH: paint | 5 | 1 | Wall Finish 1 | [WLWA-004]
OVBR | Overnight Stay - Bedroom | Staff Amenities | FIN | WLPR-001 | WALL PROTECTION: bedhead wall panel, full height | 1 | 1 | Wall Protection | [WLPR-001]