## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
PAR | Parenting Room | Sanitary Facilities | Translation and QA Only | 9 | 2700 |  | 5 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1-2 persons intermittently;;; | The Parenting Room provides an enclosed, lockable room with the amenities required for parents to feed and change babies including a changing table, waste bin, sink, and arm chair. Access and clearance for prams is required. | ~ The Parenting Room should be located to have ready access to other public amenities sanitary facilities and is often collocated with waiting areas. ~ Inclusion of a small fridge within the room may be considered if the room is located to serve a staff area; provision will be dependent on operational policies. ~ This Standard Component shows a wall mounted drop-down change table. Custom joinery for baby changing facilities may be considered and provision is to be determined at project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to suit local security and WHS policies and operational service requirements. | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
PAR | Parenting Room | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
PAR | Parenting Room | Sanitary Facilities | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
PAR | Parenting Room | Sanitary Facilities | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
PAR | Parenting Room | Sanitary Facilities | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
PAR | Parenting Room | Sanitary Facilities | D+W | DOHI-002.01 | DOOR: hinged, 1 leaf, 850 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-001] with privacy latch, emergency release required if inward opening door
PAR | Parenting Room | Sanitary Facilities | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
PAR | Parenting Room | Sanitary Facilities | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012]
PAR | Parenting Room | Sanitary Facilities | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to sink
PAR | Parenting Room | Sanitary Facilities | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to sink
PAR | Parenting Room | Sanitary Facilities | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 1 |  | [FIHR-026]
PAR | Parenting Room | Sanitary Facilities | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010] tiles acceptable if tiled floor is provided
PAR | Parenting Room | Sanitary Facilities | FIN | FLVY-111 | FLOOR FINISH: vinyl, seamless, non-slip | 1 | 1 | Floor Finish 1 | [FLVY-003] minimum slip rating R10/pendulum P3 or agreed equivalent; tiles are also acceptable
PAR | Parenting Room | Sanitary Facilities | FFE | FQBS-261 | ARMCHAIR: visitor, waiting areas | 1 | 1 |  | [FQBS-010] to be suitable for breastfeeding
PAR | Parenting Room | Sanitary Facilities | FFE | FQGE-361 | CHANGE TABLE: baby, wall mounted | 1 | 1 |  | [FQBS-035]
PAR | Parenting Room | Sanitary Facilities | FFE | FQTA-401 | TABLE: round, 450H, 500 diameter | 1 | 1 |  | [FQTA-049]
PAR | Parenting Room | Sanitary Facilities | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
PAR | Parenting Room | Sanitary Facilities | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1 |  | [FQCW-019] for nappies, dedicated sanitary waste stream may be required depending on local waste management policies, size to suit operation policies regarding frequency of waste removal
PAR | Parenting Room | Sanitary Facilities | FFE | HYBA-302 | SINK: single bowl, accessible | 1 | 1 |  | [HYBA-051] depth to meet accessibility requirements when combined with joinery shroud; provision of an integrated solid surface sink in a solid surface bench is also acceptable
PAR | Parenting Room | Sanitary Facilities | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to sink
PAR | Parenting Room | Sanitary Facilities | FFE | HYTP-152 | TAPWARE: sink, mixer, fixture mounted, accessible | 1 | 1 |  | [HYTP-040]
PAR | Parenting Room | Sanitary Facilities | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to sink tapware
PAR | Parenting Room | Sanitary Facilities | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to sink tapware
PAR | Parenting Room | Sanitary Facilities | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]
PAR | Parenting Room | Sanitary Facilities | FFE | JOBE-041 | BENCH: 650D, laminate | 1 | 1 |  | [FIJO-232] solid surface material is also acceptable
PAR | Parenting Room | Sanitary Facilities | FFE | JOBE-221 | BENCH SUPPORT: end panel | 1 | 1 |  | [FIJO-213]
PAR | Parenting Room | Sanitary Facilities | FFE | JOGE-037 | SHROUD: under bench, removable, accessible | 1 | 1 |  | [FIJO-228] to bench to conceal plumbing for sink
PAR | Parenting Room | Sanitary Facilities | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
PAR | Parenting Room | Sanitary Facilities | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 4 | 1 | Wall Finish 2 | [WLWA-020]
PAR | Parenting Room | Sanitary Facilities | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | [WLWA-007] to bench with sink