## Room Data
Standard Components - Room Data Sheet
Date of issue: 28.05.2019
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
PBAT | Patient Bay, Emergency - Ambulance Triage | 6.5 | 24 Hours | 1 patient; 1-2 staff intermittently |  |  | A Patient Bed Bay used for assessment of patients on arrival by ambulance to the emergency department Ambulance Triage. The patient bay may be one of a number within the Ambulance Triage area. The patient bay constitutes a component of the Ambulance Triage area; it requires direct access and observation from write up facilities for ambulance, triage and administrative staff. It will also require direct access to a staff handwashing basin. Negative pressure requirements are for general directional airflow only. Air conditioning to be non recirculating.

## Items
Standard Components - Items in room
Date of issue: 28.05.2019
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
PBAT | Patient Bay, Emergency - Ambulance Triage | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | default = set plasterboard; drop in tile ceiling also acceptable
PBAT | Patient Bay, Emergency - Ambulance Triage | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FFE | FIHR-019 | BRACKET: for suction bottle | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FFE | FQBS-028 | CHAIR: visitor, clinical areas | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FFE | FIRT-025 | TRACK: curtain, bedscreen, U shaped | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FFE | FQGE-009 | CURTAIN: bed screen | 2
PBAT | Patient Bay, Emergency - Ambulance Triage | FFE | MGFP-004 | FLOWMETER: oxygen | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FFE | MMGE-142 | TROLLEY: sharps bin | 1 | shared
PBAT | Patient Bay, Emergency - Ambulance Triage | FFE | MMGE-002 | ADAPTER: suction | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FFE | MMGE-100 | SUCTION BOTTLE | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1 | shared
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | ELPR-006 | RCD: residual current device | 1 | on service panel
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | LIFX-030 | LIGHT: downlight, recessed, compact fluorescent | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel + indicator button & light
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | ELBO-015 | SWITCH: light, single | 1 | on services panel for examination downlight
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | MGAS-062 | OUTLET: suction, on services panel | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on services panel + indicator button & light
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | shared between a group of beds
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | ITSE-006 | BUTTON: duress, fixed | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 | flush mounted
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | ELGP-122 | GPO: emergency power, single, on services panel | 2 | on services panel