## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
PBC-24 | Patient Bay - Critical, 24m2 | 24 | 24 Hours | 1 patient, 1-2 visitors, Up to 6-8 staff |  | Acoustic privacy is required | A Single Bed Bay for patient requiring critical care nursing and medical treatment. Visual access to Staff Station is required. Screen curtains are required for patient privacy. Maximum natural light is required to patient beds.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
PBC-24 | Patient Bay - Critical, 24m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 |  | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FA | DWOB-003 | OBSERVATION: internal window, alum/glass, double glazed, integral venetian blind, powdercoat | 1 | to partition walls | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | DWWD-007 | BLIND: venetian, integral | 2 | to windows, controls to both sides | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FA | DWWH-005 | WINDOW | 1 | desirable | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | ELGP-101 | GPO: single, ceiling mounted | 3 | For TV, clock, proc light | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | ELGP-104 | GPO: single, on pendant | 12 | on tandem pendant | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 |  | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | ELGP-121 | GPO: emergency power, single, on pendant | 12 | on tandem pendant | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | ELGP-204 | GPO: double, on pendant | 2 | on single pendant | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | ELGP-208 | GPO: double, wall mounted | 2 | to walls | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 1 | to dialysis station | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | ELPR-006 | RCD: residual current device | 1 | on tandem pendant | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | FIBM-018 | WHITEBOARD: fixed | 1 | 600mm x 600mm | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 |  | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1 |  | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | FIHR-012 | BRACKET: for monitor, cardiac | 1 | mounted on pendant | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | FIHR-016 | BRACKET: for sharps bin | 1 | mounted to trolley | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | FIRT-023 | TRACK: curtain, bedscreen, L shaped | 1 |  | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 |  | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | FQBS-022 | CHAIR: recliner, clinical | 1 | patient - intermittent use | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | FQBS-031 | CHAIR: visitor, patient, stackable | 1 |  | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | FQBS-052 | STOOL: mobile, high, adj height | 1 | for staff | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | FQCW-004 | BIN: waste, clinical, 120L | 1 |  | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | FQCW-043 | BIN: waste, sharps, on trolley | 1 |  | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | FQGE-009 | CURTAIN: bed screen | 1 |  | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | FQSM-016 | TROLLEY | 1 |  | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | FQTA-013 | TABLE: overbed | 1 |  | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | HYBA-009 | BASIN: handwash, Type A, scrub | 1 | refer BHWS-A (similar) | No | No | Yes | No | Yes | Yes | Yes | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | HYDR-006 | DRAIN: tundish | 1 |  | No | No | No | No | No | No | Yes | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | HYTP-015 | OUTLET: reverse osmosis (RO) water | 1 |  | No | No | Yes | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin | No | No | Yes | No | Yes | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1 |  | Yes | Yes | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on tandem pendant, + indicator button & light | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on tandem pendant, + indicator button & light | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on tandem pendant, + indicator button & light | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | ITCL-016 | CLOCK: clock system slave, analogue | 1 | ceiling mounted, master clock system | Yes | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on tandem pendant, call button on the handset | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | ITIN-014 | OUTLET: data, single RJ45, on pendant | 1 | on tandem pendant, for monitor communications with associated cabling and connections; verify outlet type/s with monitor selected | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | ITIN-024 | OUTLET: data, double RJ45, on pendant | 1 | on tandem pendant | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | ITIN-024 | OUTLET: data, double RJ45, on pendant | 1 | on single pendant | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 outlet for telephone | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | ITIN-070 | OUTLET: MATV | 1 |  | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1 | to staff work area | No | Yes | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | LIFX-017 | LIGHT: night light | 1 |  | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1 |  | Yes | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | MGAS-021 | OUTLET: medical air (MA), on pendant | 2 | on tandem pendant | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | MGAS-041 | OUTLET: oxygen (O2), on pendant | 4 | on tandem pendant | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | SE | MGAS-061 | OUTLET: suction, on pendant | 4 | on tandem pendant | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | MGFP-002 | FLOWMETER: medical air | 2 | to pendant | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | MGFP-004 | FLOWMETER: oxygen | 4 | to pendant | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | MMBE-014 | BED: patient, ICU, electric with mattress | 1 |  | Yes | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | MMGE-002 | ADAPTER: suction | 4 | to pendant | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | MMGE-033 | FLOWCHART STAND: mobile | 1 |  | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1 |  | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | MMGE-096 | STATION: dialysis | 1 | with RO water & tundish drain | No | No | Yes | No | Yes | Yes | Yes | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | MMGE-100 | SUCTION BOTTLE | 4 | to pendant | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | MMHA-001 | CARRIER: suction bottle | 1 | mobile | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | MMHA-030 | MONITOR: patient, cardiac, pendant mounted | 1 |  | Yes | Yes | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | MMSP-020 | PENDANT: tandem, wet and dry combination (fixed or adjustable height) | 1 |  | Yes | Yes | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FFE | MMSP-023 | PENDANT: single, power and data | 1 |  | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FA | WLPR-013 | WALL PROTECTION: corner guards, to 1500 AFFL, prefinished PVC | 1 | Equal to 'Acrovyn' | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
PBC-24 | Patient Bay - Critical, 24m2 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin, tiles also acceptable | No | No | No | No | No | No | No | No | No