## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Briefing
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics | Description / Special Requirements
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | 20 |  | 1 patient, 1-2 visitors, Up to 6-8 staff | 24 Hours | Acoustic privacy is required | An enclosed single Bed Bay for a patient requiring critical care nursing and medical treatment, suitable for Role Delineation Levels 2 to 4 (20m2) / Levels 5 & 6 (25m2) health care facilities; Visual access to Staff Station is required; Screen curtains are required for patient privacy. Maximum natural light is required to patient beds. Acoustics: Acoustic privacy is required. Cardiac Protected Electrical Area

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
[7 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FE | FE-15985 | Dialysis station | 1 | RO water outlet & tundish drain |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FE | FE-3100 | Basin - scrub, Type A | 1 |  |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FE | FE-36050 | Monitor - cardiac | 1 | on services pendant |  |  |  | Yes | Yes | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FE | FE-54520 | Telephone - handset, handsfree | 1 | wall phone |  |  |  | No | Yes | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FE | FF-5547 | Patient entertainment | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FE | FF-5992 | Lifter - patient, sling | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FE | FF-39155 | Patient lifter, ceiling mounted | 1 | Optional. H-track. |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FE | FF-6479 | Chair - recliner, electric | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FE | FE-5854 | Bed - ICU, electric + patient mattress | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FE | FE-5855 | Clock - electric | 1 | Master clock system |  |  |  | Yes | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FE | FE-5856 | Computer on wheels | 1 | CIS. Or wall mounted, optional. If wall mounted add bracket. |  |  |  | Yes | Yes | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FE | FE-5857 | Light - procedures small, ceiling | 1 | Or on pendant |  |  |  | Yes | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FE | FE-5858 | Pump - infusion | 1 | Number and type per bed to be confirmed to suit project specific requirements.. |  |  |  | Yes | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FE | FE-5859 | Services pendant - 2 arm | 1 |  |  |  |  | Yes | Yes | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-1090 | Bench - laminate, free standing | 1 | optional |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-12300 | Linen carrier - dirty, single | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-1465 | Bracket - suction bottle | 2 | On pendant |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-150 | Air flowmeter | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-16200 | Table - overbed | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-16250 | Oxygen flowmeter | 4 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-21700 | Stool - adjustable, mobile, high | 1 | for staff |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-21950 | Suction adapter | 4 | On pendant |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-22000 | Suction bottle | 2 | On pendant |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-23950 | Trolley | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-2610 | Chair - visitor, stackable | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-4600 | Curtain track - bed screen | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-5000 | Curtain - bed screen | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-6152 | Dispenser - disposable glove | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-6154 | Dispenser - paper/ hand towel | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-6156 | Dispenser - soap | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-6158 | Dispenser - soap antiseptic | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-8070 | Flowchart stand - mobile | 1 | Not required with electronic medical records |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-5825 | Bracket - patient entertainment, ceiling | 1 | In accordance with ICT policy. |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-6153 | Dispenser - moisturiser | 1 | Depends on Operational Policy. |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-5830 | Dispenser - antiseptic hand rub | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-5824 | Waste bin - general | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-5975 | Waste bin - clinical | 1 | Size, number and type depends on Waste Management policy. |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-24405 | Whiteboard - magnetic | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-5550 | Blind - integral | 4 | To windows, controls to both sides of internal observation windows. Number to align with window configuration. |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-5591 | Bracket - cardiac monitor | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-10900 | IV pole | 1 | On pendant, number to suit. |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | FF | FF-5993 | Sharps bin; on trolley | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-9000 | GPO: Single | 12 | to services pendant |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-9000 | GPO: Single | 2 | Patient entertainment system, proc light |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-9010 | GPO: Emergency power, single (V) | 10 | to services pendant |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-9010 | GPO: Emergency power, single (V) | 1 | dialysis machine |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-9001 | GPO: Double | 2 | 2 - walls |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-9015 | GPO: Cleaner | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-9030 | Cardiac protected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-9050 | Direct connection | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-2089 | GPO: Uninterripted power single | 2 | To services pendant |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-1080 | Clock: master clock | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-1005 | Voice / Data outlet: single | 1 | Wall telephone |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-1006 | Voice / Data outlet: double | 1 | services pendant |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-1006 | Voice / Data outlet: double | 3 | 1-wall (computer on wheels), 2-services pendant. |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-1090 | TV: MATV | 1 | May be replaced with data outlet, in accordance with ICT policy |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-1120 | Monitor connection facilities and cabling | 1 | Cardiac monitor |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-4037 | Tundish drain | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-4045 | Reverse osmosis (RO) water outlet | 1 | Dialysis |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-6001 | General: colour corrected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-6200 | Light switches | 2 | 1 x room (inc dimmer) 1 x procedure light |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-6060 | Special: night lights | 2 | wall washers |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-8000 | Patient/ Staff call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-8005 | Patient call handset | 1 | call button on the handset |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-8080 | Emergency call | 1 | + indicator button & light |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-1951 | Staff assist call | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-7000 | Oxygen (O2) | 4 | to services pendant |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-7020 | Medical Air (MA) | 2 | to services pendant |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | SE | S-7040 | Suction | 4 | to services pendant |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | Fabrics | 1000 | Floor finish | 1 |  | Vinyl | Standard slip resistant | Seamless, coved | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | Fabrics | 2526 | Floor finish | 1 | Under basin. Significant change in colour to be avoided. | Vinyl | Non-slip | Seamless coved | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | Fabrics | 3060 | Wall finish | 1 | behind basin. Selection of material to comply with Part D Infection Prevention and Control AusHFG. | Vinyl | Prefinished | Splashback | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | Fabrics | 2535 | Wall protection | 1 |  |  |  | Corner guards to 900 AFFL | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | Fabrics | 5010 | Ceiling - Plasterboard | 1 | Acoustic tiles acceptable if ceiling mounted lifter is not required and room is not negatively pressured. | Plasterboard | Paint, washable | Flush set, suspended | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | Fabrics | 7001 | Windows | 1 | Natural light & outlook essential |  |  |  | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | Fabrics | 2719 | Doors | 1 |  | Alum/Glass | Anodised | Triple leaf, fully glazed, sliding safety glass | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | Fabrics | 2720 | Observation | 1 | Optional, to rooms with an outboard ensuite. | Alum/ Glass | Powdercoat | Internal window, double partition walls with internal blinds | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
PBCE-20 | Patient Bay - Critical (Enclosed), 20m2 | Fabrics | 2000 | Skirting | 1 |  | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No