## Room Data
Standard Components - Room Data Sheet
Date of issue: 28.05.2019
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
PBIC | Patient Bay - Intensive Care | 24.5 | 24 Hours | 1 patient, 1 visitor, Up to 6-8 staff |  | Acoustic attenuation is required | An acuity adaptable, open bed bay for a patient requiring intensive medical treatment, nursing care and monitoring for potentially life threatening conditions. Visual access to a main Staff Station or Sub Staff Station is required. Screen curtains are required for patient privacy. Natural light is required to patient beds. Dialysis facilities may be required, assumed to be provided via mobile reverse osmosis water dialysis units. Mobile imaging may be required, shielding requirements must be confirmed with Radiation Consultant.

## Items
Standard Components - Items in room
Date of issue: 28.05.2019
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
PBIC | Patient Bay - Intensive Care | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
PBIC | Patient Bay - Intensive Care | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
PBIC | Patient Bay - Intensive Care | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
PBIC | Patient Bay - Intensive Care | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
PBIC | Patient Bay - Intensive Care | FA | WLPR-013 | WALL PROTECTION: corner guards, to 1500 AFFL, prefinished PVC | 4
PBIC | Patient Bay - Intensive Care | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
PBIC | Patient Bay - Intensive Care | FA | DWWH-005 | WINDOW | 1
PBIC | Patient Bay - Intensive Care | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PBIC | Patient Bay - Intensive Care | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 5
PBIC | Patient Bay - Intensive Care | FFE | MGFP-002 | FLOWMETER: medical air | 3 | on tandem pendant
PBIC | Patient Bay - Intensive Care | FFE | DWWD-007 | BLIND: venetian, integral | 1 | to window
PBIC | Patient Bay - Intensive Care | FFE | FIHR-019 | BRACKET: for suction bottle | 4 | on tandem pendant
PBIC | Patient Bay - Intensive Care | FFE | FQBS-019 | CHAIR: office, ergonomic, high | 1 | for staff
PBIC | Patient Bay - Intensive Care | FFE | MMGE-019 | CHAIR: patient | 1
PBIC | Patient Bay - Intensive Care | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PBIC | Patient Bay - Intensive Care | FFE | FQCW-035 | BIN: waste, recycling, plastics, 50L | 1
PBIC | Patient Bay - Intensive Care | FFE | FIRT-025 | TRACK: curtain, bedscreen, U shaped | 1
PBIC | Patient Bay - Intensive Care | FFE | FQGE-009 | CURTAIN: bed screen | 2
PBIC | Patient Bay - Intensive Care | FFE | FQCW-016 | BIN: waste, general, 20L | 1
PBIC | Patient Bay - Intensive Care | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1
PBIC | Patient Bay - Intensive Care | FFE | FQCW-004 | BIN: waste, clinical, 120L | 1
PBIC | Patient Bay - Intensive Care | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | near entry
PBIC | Patient Bay - Intensive Care | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
PBIC | Patient Bay - Intensive Care | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
PBIC | Patient Bay - Intensive Care | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
PBIC | Patient Bay - Intensive Care | FFE | MMOP-027 | IV POLE: on pendant | 1
PBIC | Patient Bay - Intensive Care | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
PBIC | Patient Bay - Intensive Care | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 1
PBIC | Patient Bay - Intensive Care | FFE | FQTA-013 | TABLE: overbed | 1
PBIC | Patient Bay - Intensive Care | FFE | MGFP-004 | FLOWMETER: oxygen | 4 | on tandem pendant
PBIC | Patient Bay - Intensive Care | FFE | MMGE-142 | TROLLEY: sharps bin | 1
PBIC | Patient Bay - Intensive Care | FFE | FQSN-006 | BIN: storage bins, for wall mounted panel | 3 | wire basket bins
PBIC | Patient Bay - Intensive Care | FFE | MMGE-002 | ADAPTER: suction | 4 | on tandem pendant
PBIC | Patient Bay - Intensive Care | FFE | MMGE-100 | SUCTION BOTTLE | 4 | on tandem pendant
PBIC | Patient Bay - Intensive Care | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
PBIC | Patient Bay - Intensive Care | FFE | HYBA-009 | BASIN: handwash, Type A, scrub | 1
PBIC | Patient Bay - Intensive Care | FFE | MMBE-013 | BED: patient, ICU, electric | 1
PBIC | Patient Bay - Intensive Care | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
PBIC | Patient Bay - Intensive Care | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1
PBIC | Patient Bay - Intensive Care | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 1 | optional
PBIC | Patient Bay - Intensive Care | FFE | MMSP-020 | PENDANT: tandem, wet and dry combination (fixed or adjustable height) | 1 | with drawer for patient property
PBIC | Patient Bay - Intensive Care | FFE | ITCL-014 | CLOCK: analogue, electric | 1
PBIC | Patient Bay - Intensive Care | FFE | MMGE-049 | MACHINE: dialysis | 1 | optional, if mobile dialysis required
PBIC | Patient Bay - Intensive Care | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1
PBIC | Patient Bay - Intensive Care | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1
PBIC | Patient Bay - Intensive Care | FFE | MMHA-023 | VENTILATOR | 1 | on pendant 1-A
PBIC | Patient Bay - Intensive Care | FFE | ITBU-006 | CONTROL PANEL: patient entertainment, handset | 1 | on tandem pendant
PBIC | Patient Bay - Intensive Care | FFE | FIJO-031 | BENCH: 750D, open under, laminate finish | 1
PBIC | Patient Bay - Intensive Care | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 1 | optional
PBIC | Patient Bay - Intensive Care | FFE | MMHA-030 | MONITOR: patient, cardiac, pendant mounted | 1 | on tandem pendant
PBIC | Patient Bay - Intensive Care | FFE | FQBS-055 | CHAIR: overnight fold out | 1 | can optionally be a visitor chair
PBIC | Patient Bay - Intensive Care | FFE | FIJO-213 | PANEL: joinery carcass end | 1
PBIC | Patient Bay - Intensive Care | FFE | FQSM-043 | TROLLEY: nested, set of 3, underbench | 1
PBIC | Patient Bay - Intensive Care | FFE | MMBE-068 | LIFTER: patient, pendant mounted | 1 | optional
PBIC | Patient Bay - Intensive Care | FFE | MMGE-178 | PROCESSOR: reverse osmosis RO water, mobile | 1 | optional if mobile dialysis required
PBIC | Patient Bay - Intensive Care | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1
PBIC | Patient Bay - Intensive Care | SE | ELPR-006 | RCD: residual current device | 2 | on tandem pendant
PBIC | Patient Bay - Intensive Care | SE | ELGP-101 | GPO: single, ceiling mounted | 2 | display screen, clock
PBIC | Patient Bay - Intensive Care | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on tandem pendant, + indicator button & light
PBIC | Patient Bay - Intensive Care | SE | HYTP-008 | OUTLET: cold water | 1 | optional, for mobile reverse osmosis water unit
PBIC | Patient Bay - Intensive Care | SE | LIFX-017 | LIGHT: night light | 1 | wall washers
PBIC | Patient Bay - Intensive Care | SE | ELBO-015 | SWITCH: light, single | 1
PBIC | Patient Bay - Intensive Care | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on tandem pendant, + indicator button & light
PBIC | Patient Bay - Intensive Care | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on tandem pendant, call button on the handset
PBIC | Patient Bay - Intensive Care | SE | ITCL-004 | BUTTON: nurse call, emergency | 2 | on tandem pendant, + indicator button & light
PBIC | Patient Bay - Intensive Care | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 3 | optional, if mobile dialysis station required
PBIC | Patient Bay - Intensive Care | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
PBIC | Patient Bay - Intensive Care | SE | ELPR-004 | MONITOR: line isolation | 1
PBIC | Patient Bay - Intensive Care | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1
PBIC | Patient Bay - Intensive Care | SE | ELBO-005 | EQUIPOTENTIAL JUNCTION BOX | 1
PBIC | Patient Bay - Intensive Care | SE | ELBO-012 | SWITCH: light, dimmer | 2 | one on pendant, one to wall
PBIC | Patient Bay - Intensive Care | SE | ITIN-014 | OUTLET: data, single RJ45, on pendant | 6 | on tandem pendant
PBIC | Patient Bay - Intensive Care | SE | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | optionally can be a data outlet for patient entertainment system
PBIC | Patient Bay - Intensive Care | SE | MGAS-021 | OUTLET: medical air (MA), on pendant | 3 | on tandem pendant
PBIC | Patient Bay - Intensive Care | SE | MGAS-041 | OUTLET: oxygen (O2), on pendant | 4 | on tandem pendant
PBIC | Patient Bay - Intensive Care | SE | MGAS-061 | OUTLET: suction, on pendant | 4 | on tandem pendant
PBIC | Patient Bay - Intensive Care | SE | ELGP-132 | GPO: UPS, single, on pendant | 4 | on tandem pendant
PBIC | Patient Bay - Intensive Care | SE | ELGP-121 | GPO: emergency power, single, on pendant | 16 | on tandem pendant
PBIC | Patient Bay - Intensive Care | SE | ELGP-125 | GPO: emergency power, single, ceiling mounted | 1
PBIC | Patient Bay - Intensive Care | SE | ELPR-007 | UPS: status indicator | 2 | on tandem pendant
PBIC | Patient Bay - Intensive Care | SE | HYDR-015 | DRAIN: tundish unit, integral drainage outlets | 1 | optional, if mobile dialysis required
PBIC | Patient Bay - Intensive Care | SE | HYDR-016 | DRAIN: floor waste, sealed | 1