## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
PBSC | Patient Bay - Specimen Collection | Pathology | Translation and QA Only | 9 | 2700 | SPECC | 4 | 07.04.2026 |  | 8am to 6pm, daily (may vary depending on service requirements) | 1 patient; 1 visitor; 1 staff | A Patient Bay used for the collection of specimens to be transferred to a laboratory for testing. | ~ Ready access to a handwashing basin is required. ~ Ready access may be required to a pneumatic tube bay that is in a staff supervised area. ~ Recliner must be able to lay flat to support the patient in the event of an adverse reaction (e.g. fainting). ~ A desk may be provided in lieu of Workstation on Wheels depending on operational model. ~ An operational model for responding to calls from staff/patients will be needed to support the inclusion of a nurse call system and is to be determined based on service requirements. ~ A risk assessment should be undertaken to inform staff safety requirements with adjoining cubicles which may require adjustments to the design and/or operational strategies, such as the use of mobile duress systems. ~ Refer to the Pathology HPU for paediatric requirements. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 3 |  | [FIHR-026] optional, prioritize lower hook for wheelchair users if only one hook provided
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016] on trolley
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | [FIHR-033]
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FIRT-051.01 | TRACK: curtain, privacy, straight | 1 | 1 |  | [FIRT-031]
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 3 |  | [FQBS-028] optional
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 1 |  | [FQBS-051]
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | [FQGE-010]
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 1 | 1 |  | [FQSN-007] extent and type of storage to be based on service requirements and local infection control policies
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044] on trolley; may be wall mounted or mobile
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016]
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | [ITNE-008+MMGE-164] a desk may be provided depending on operational model
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | ITNE-316 | PRINTER: labels, small, desktop | 1 | 3 |  | [FQGE-056] optional, on WOW
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 3 |  | [LIFX-027] optional
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | MMBE-094 | CHAIR: patient, recliner, clinical, phlebotomy, electric | 1 | 1 |  | [MMBE-094] height adjustable and able to lie flat, electric examination couch may also be provided
PBSC | Patient Bay - Specimen Collection | Pathology | FFE | MMTR-087 | TROLLEY: phlebotomy, 600W x 490D x 900H nom | 1 | 1 |  | [MMGE-189] with drop down shelf
PBSC | Patient Bay - Specimen Collection | Pathology | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
PBSC | Patient Bay - Specimen Collection | Pathology | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
PBSC | Patient Bay - Specimen Collection | Pathology | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 5 | 1 | Floor Skirting | [FLSK-010]
PBSC | Patient Bay - Specimen Collection | Pathology | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
PBSC | Patient Bay - Specimen Collection | Pathology | FIN | WLFI-001 | WALL FINISH: paint | 3 | 1 | Wall Finish 1 | [WLWA-004]
PBSC | Patient Bay - Specimen Collection | Pathology | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 3 | 1 | Wall Finish 2 | [WLWA-020]
PBSC | Patient Bay - Specimen Collection | Pathology | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 1 | Wall Protection | [WLPR-006]
PBSC | Patient Bay - Specimen Collection | Pathology | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] to chair
PBSC | Patient Bay - Specimen Collection | Pathology | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 3 |  | [ELGP-101] optional, to exam light
PBSC | Patient Bay - Specimen Collection | Pathology | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
PBSC | Patient Bay - Specimen Collection | Pathology | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | [ELPR-006]
PBSC | Patient Bay - Specimen Collection | Pathology | SER | ELSW-001 | SWITCH: light | 1 | 3 |  | [ELBO-015] optional, to exam light
PBSC | Patient Bay - Specimen Collection | Pathology | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008]
PBSC | Patient Bay - Specimen Collection | Pathology | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004]
PBSC | Patient Bay - Specimen Collection | Pathology | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
PBSC | Patient Bay - Specimen Collection | Pathology | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]