## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | 12 | 24 Hours | 1 patient; 1 - 2 staff |  |  | The Patient Bed Bay Acute Treatment may be used for assessment and treatment of patients with acute conditions and will be located within the Emergency Unit. The Bay may have partition side walls; glazing is recommended. The Patient Bay will have close access to a staff handwashing basin.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FA | DWOB-003 | OBSERVATION: internal window, alum/glass, double glazed, integral venetian blind, powdercoat | 1 | to partition walls, if provided | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | DWWD-007 | BLIND: venetian, integral | 2 | to internal windows if provided | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | SE | ELBO-015 | SWITCH: light, single | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | exam light | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | SE | ELGP-105 | GPO: single, on services panel | 3 | on services panel | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | SE | ELGP-109 | GPO: single, wall mounted | 1 | for electric bed | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 3 | on services panel | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | for monitor, if required | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | SE | ELGP-206 | GPO: double, on services panel, RCD protected | 1 | on services panel | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | FIHR-011 | BRACKET: for monitor | 1 | optional, may have ergonomic arm | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | FIHR-016 | BRACKET: for sharps bin | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | FIHR-019 | BRACKET: for suction bottle | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 1 | optional, for storage | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | FIJO-020 | BENCH: 600D, open under, laminate finish | 1 | optional, freestanding | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | FIJO-194 | SHELF: laminate | 1 | above services panel, optional | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | FIRT-020 | TRACK: ceiling mounted, IV | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | FIRT-024 | TRACK: curtain, bedscreen, straight | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | FQBS-030 | CHAIR: visitor, patient | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | FQGE-009 | CURTAIN: bed screen | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | FQSM-016 | TROLLEY | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | FQSN-006 | BIN: storage bins, for wall mounted panel | 10 | optional, for storage on louvred panel | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on services panel, + indicator button & light | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, + indicator button & light | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, + indicator button & light | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | call button on the handset | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | optional, if networked monitoring required, with associated cabling; verify outlet type/s with monitor selected | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | on services panel, 1 outlet for telephone | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | SE | ITIN-070 | OUTLET: MATV | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | LIFX-013 | LIGHT: procedure, ceiling mounted, small | 1 |  | Yes | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | on services panel, optional | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | on services panel, optional, if N2O provided | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | MGFP-002 | FLOWMETER: medical air | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | MGFP-004 | FLOWMETER: oxygen | 2 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | MMBE-014 | BED: patient, ICU, electric with mattress | 1 |  | Yes | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | MMGE-002 | ADAPTER: suction | 2 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | MMGE-031 | DIAGNOSTIC SET: wall mounted | 1 | optional | Yes | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | MMGE-039 | HANGER: IV, for ceiling track | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | MMGE-100 | SUCTION BOTTLE | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | MMGE-123 | TROLLEY: instrument | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FFE | MMHA-008 | MONITOR: patient, cardiac with vital signs | 1 | optional | Yes | Yes | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FA | WLPR-002 | WALL PROTECTION: bed protection wall panel, composite, laminate finish | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FA | WLPR-013 | WALL PROTECTION: corner guards, to 1500 AFFL, prefinished PVC | 1 | As required, Equal to 'Acrovyn' | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FA | WLPR-019 | WALL PROTECTION: crash rail, at 900 AFFL, prefinished PVC | 1 | As required, Equal to 'Acrovyn' | No | No | No | No | No | No | No | No | No
PBTR-A12 | Patient Bay - Acute Treatment, 12m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No