## Room Data
Standard Components - Room Data Sheet
Date of issue: 28.05.2019
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
PBTR-FT | Patient Bay, Emergency - Fast Track | 6.5 | 24 Hours | 1 patient; 1-2 staff intermittently |  |  | A short stay patient bay used for assessment and treatment of patients with non acute conditions. The patient bay will have close access to a staff handwashing basin and patient toilet.

## Items
Standard Components - Items in room
Date of issue: 28.05.2019
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
PBTR-FT | Patient Bay, Emergency - Fast Track | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 2
PBTR-FT | Patient Bay, Emergency - Fast Track | FA | WLWA-021 | WALL FINISH: vinyl, to 1800 AFFL | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | MGFP-002 | FLOWMETER: medical air | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | FIHR-019 | BRACKET: for suction bottle | 2
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | FQBS-030 | CHAIR: visitor, patient | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | FIHR-026 | HOOK: coat | 2 | optional
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | FIRT-025 | TRACK: curtain, bedscreen, U shaped | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | FQGE-009 | CURTAIN: bed screen | 2
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | shared
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | FIDI-014 | DISPENSER: disposable glove | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | MGFP-004 | FLOWMETER: oxygen | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | MMGE-142 | TROLLEY: sharps bin | 1 | shared
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | FQSN-006 | BIN: storage bins, for wall mounted panel | 3
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | MMGE-002 | ADAPTER: suction | 2
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | MMGE-100 | SUCTION BOTTLE | 2
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | LIFX-013 | LIGHT: procedure, ceiling mounted, small | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | MMGE-031 | DIAGNOSTIC SET: wall mounted | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | FFE | MMBE-023 | COUCH: examination, electric, mobile | 1 | optional, may be replaced with a patient chair or recliner
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ELPR-006 | RCD: residual current device | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel + indicator button & light
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ELBO-015 | SWITCH: light, single | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | MGAS-062 | OUTLET: suction, on services panel | 2
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel + indicator button & light
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, call button on the handset
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on services panel + indicator button & light
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | shared between a group of beds
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | MMSP-026 | SERVICES PANEL: wall mounted | 2
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | ELGP-125 | GPO: emergency power, single, ceiling mounted | 1