## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | Translation and QA Only | 9 | 2700 | TRMT-RD-B | 4 | 07.04.2026 |  | 7am to 9pm, daily (may vary depending on service requirements) | 1 patient; 1 visitor; 1-2 staff intermittently | The Patient Bay - Renal Dialysis is for patients receiving haemodialysis therapy. Treatments for each patient may take from 3 to 6 hours, occurring up to 3 days per week. | ~ A staff handwashing basin will be provided for each 4 bays and the Patient Bay will have, wherever possible, clear line of sight to a staff station. ~ Access to natural light and views is required. ~ Furniture and furnishings should provide a high level of patient comfort and amenity. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | D+W | AHWCV-001 | WINDOW COVERING: blind, roller, single | 1 | 1 | External - Window 1 | [DWWD-004]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | D+W | WIFX-161.01 | WINDOW: fixed, external, double glazed, sill at 1500H | 1 | 1 | External - Window 1 | [DWWH-005] access to natural light and external outlook essential
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1 |  | [FIHR-019]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | FIHR-214 | BRACKET: computer display screen, single, articulated, ceiling mounted | 1 | 1 |  | [FIHR-004]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-032]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1 |  | [FQBS-030]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1 |  | [FQGE-010]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1 |  | [FQTA-013]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | ITCL-301 | DISPLAY SCREEN: patient entertainment system | 1 | 1 |  | [ITBU-012]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | LIFX-113 | LIGHT: examination, single articulated arm, 1 light head, ceiling mounted | 1 | 3 |  | [LIFX-027] optional
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | MMBE-101 | BED: patient, electric, with mattress | 1 | 1 |  | [MMBE-009]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | [MMGE-100]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FFE | MMGE-381 | MACHINE: dialysis | 1 | 1 |  | [MMGE-049]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 7 | 1 | Floor Skirting | [FLSK-010]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / pendulum P3 or agreed equivalent; a higher slip rating may be required depending on local WHS policies
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 2 | 3 | Wall Finish 2 | [WLWA-020] optional, to side walls if provided
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FIN | WLPR-001 | WALL PROTECTION: bedhead wall panel, full height | 1 | 1 | Wall Protection | [WLPR-001]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | FIN | WLPR-006 | WALL PROTECTION: corner guards | 2 | 3 | Wall Protection | [WLPR-006] optional, to side walls if provided
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | ELGP-246 | GPO: double, emergency power, on services panel | 3 | 1 | Panel 1 | [ELGP-222]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | ELPR-073 | RCD: residual current device, on services panel | 1 | 1 | Panel 1 | [ELPR-006]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 1 | [ITCL-006] + indicator button & light
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1 | [ITCL-008] + indicator button & light
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | ITCL-253 | HANDSET: nurse call, patient to staff call, with light control, with patient entertainment system control, with speaker | 1 | 1 | Panel 1 | [ITCL-028]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1 | [MGAS-062]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1 | [MMGE-002]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | [ELGP-101] to patient entertainment system
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123] low level, to recliner
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | ELSW-001 | SWITCH: light | 1 | 3 |  | [ELBO-015] optional, to exam light if provided
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004] in case of spills, to be consolidated between multiple bays
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | HYDR-104 | TUNDISH: in wall, with viewing panel | 1 | 1 |  | [MMGE-096]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | HYDR-181 | ACCESS PANEL: waterless trap | 1 | 1 |  | [HYDR-019]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | [MMGE-096]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | HYGE-081 | WALL BOX: renal dialysis, integral tundish, with 1 water supply connection and 1 drain connection | 1 | 1 |  | [MMGE-096]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | HYTP-458 | DIRECT CONNECTION: water, reverse osmosis (RO) | 1 | 1 |  | [MMGE-096]
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside curtain
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] + indicator button & light
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | ITIN-071 | OUTLET: MATV, ceiling mounted | 1 | 1 |  | [ITIN-070] to patient entertainment system, may be replaced with data outlet depending on ICT policy
PBTR-RD-B | Patient Bay - Renal Dialysis, Bed | Renal Dialysis | SER | LIFX-161 | LIGHT: reading, wall mounted | 1 | 1 |  | [LIFX-011]