## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | Translation and QA Only | 50 | 3000 |  | 2 | 07.04.2026 |  | 8am to 8pm, daily (dependent on unit operating hours) | 1 patient;; up to 3 staff assisting | The PET-CT Imaging Room provides the area and facilities for Positron Emission Tomography-Computed Tomography (PET/CT) scanning procedures with a Control Room and Equipment Room (as required) located nearby. | ~ It is not essential that the control is directly adjacent to the Imaging Room where patients are monitored via observation cameras, however ready access is required to attend to patient needs. If the Control Room is adjacent an observation window may be provided and shielding requirements will need to be confirmed. ~ Cable pathways for services between the Control Room, Equipment Room and Imaging Room must be established and coordinated prior to construction and developed based on vendor requirements. ~ Equipment is to be installed to manufacturer's specifications with sufficient clearances for maintenance access and support structure as required. ~ The PET-CT Imaging Room must be adequately shielded to ensure that radiation doses to surrounding areas do not exceed radiation dose limits and satisfy design/dose constraints. Radiation shielding is to be as advised by a qualified Radiation Consultant to suit the practice, workload and equipment procured, and all shielding on the Standard Component is indicative only. ~ Configuration of medical gases is to be confirmed to meet clinical requirements such as the provision of anaesthetic services. ~ Dimmable lights are recommended and are to be placed to avoid glare to patients. ~ Back lit ceiling artwork may be installed for patient comfort. ~ 'X-ray in Use' lights are required outside each entry door. ~ Laser marker system for procedure planning may be required subject to model of care and equipment selected. ~ Structural assessment is required to ensure the floor will be rigid with no vibration and will accommodate the weight of the PET-CT unit. ~ Room temperature and humidity control is required. Temperature requirements for equipment are to be confirmed by the vendor, including requirement for circulated cooling water. ~ The need for and extent of emergency power and UPS must be reviewed to suit site specific requirements. UPS power is required to the PET-CT scanning and control equipment. Other emergency power and UPS requirements to be confirmed based on risk assessment considering the impact of a power outage on patient care/safety. ~ An optional laser system for patient positioning and procedure planning has been indicated and may be provided subject to service requirements. A mix of respiratory gating, surface guidance, motion management and/or patient position technologies may be considered depending on clinical/service requirements (e.g. for radiation therapy planning). The provision of these technologies is to be confirmed by the project and may have additional requirements including additional power/data, water cooling, heat load, possible increased set down, increased number of trenches/conduits, space requirements for computer cabinets in control room and additional penetrations through the suspended ceiling. Requirements to be confirmed with vendors. ~ Consideration needs to be given to the clearances of equipment and replacement part delivery routes. | TRUE | FALSE | TRUE | TRUE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 2 | [DWPR-005] to room side
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 2 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | D+W | DOHI-003.02 | DOOR: hinged, 1 leaf, 900 clear opening, solid, shielded | 1 | 1 | Internal - Door 1 | [DWSC-005] automated
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | D+W | DOHI-204.02 | DOOR: hinged, 2 leaves, 1800 clear opening, solid, shielded | 1 | 1 | Internal - Door 2 | [DWSC-034] automated
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014] near door
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FIHR-030 | HOOK: equipment, patient slide, wall mounted | 1 | 1 |  | [FIHR-030]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FIHR-091 | HOOK: anchor point, for attaching patient self-assist positioning aid, wall mounted | 1 | 1 |  | [FIHR-092]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | [FIHR-019]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1 |  | [FQBS-030]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FQCL-211 | LINEN CARRIER: dirty, single skip | 1 | 1 |  | [MMGE-048]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [MMGE-142]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FQWS-031 | CART: sharps bin, clinical | 1 | 1 |  | [MMGE-142]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | [FQCW-005]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | ITBU-441 | CLOCK: analogue display, electric, wall mounted | 1 | 1 |  | [ITCL-014]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | ITCL-431 | CAMERA: patient observation, ceiling mounted | 2 | 1 |  | [ITCL-012 + FIHR-077]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | ITCL-432 | CAMERA: patient observation, wall mounted | 1 | 1 |  | [ITCL-012 + FIHR-078]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | JOCU-021 | CUPBOARD: tall, double door | 1 | 1 |  | [FIJO-218] reinforced shelving
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | JOCU-201 | CUPBOARD: under bench, single door | 1 | 1 |  | [FIJO-141]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | JOCU-221 | CUPBOARD: under bench, double door | 3 | 1 |  | [FIJO-136]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MGFP-061 | ADAPTER: suction | 2 | 1 |  | [MMGE-002] on services panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MIGE-041 | WARMER: contrast, benchtop | 1 | 3 |  | [MMMI-377] optional
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MIGE-053 | INJECTOR: contrast, ceiling mounted | 1 | 1 |  | [MMMI-107] also may be mobile or wall mounted
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MIGE-071 | INJECTOR: radioisotope, automatic, mobile | 1 | 1 |  | [MMMI-218]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MIPT-001 | IMAGING DEVICE: PET-CT | 1 | 1 |  | [MMMI-207]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MIPT-006 | TABLE: patient, PET-CT | 1 | 1 |  | [MMMI-217]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MIPT-041 | PHANTOM: PET-CT | 1 | 1 |  | [MMMI-209] stored within shielded custom joinery
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MMBE-031 | TRANSFER AID: patient slide board, staff assisted patient transfer | 1 | 1 |  | [MMBE-042]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MMGE-045 | POLE: IV, mobile | 1 | 1 |  | [MMGE-045] may be ceiling mounted
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | [MMGE-100]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FFE | MMGE-251 | DEVICE: sphygmomanometer, portable | 1 | 1 |  | [MMGE-091]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 10 | 1 | Floor Skirting | [FLSK-010]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FIN | WLFI-011.03 | WALL FINISH: vinyl, to 1200 AFFL | 1 | 1 | Wall Finish 2 | [WLWA-025]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 6 | 1 | Wall Finish 3 | [WLWA-020]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | [WLWA-007]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1 | [ELGP-122] on service panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1 | [MGAS-022] on services panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 3 | Panel 1 | [MGAS-032] optional, on services panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | 1 | Panel 1 | [MGAS-042] on services panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 3 | Panel 1 | [MGAS-053] optional, on services panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | MSP | MGAS-062 | OUTLET: suction, on services panel | 2 | 1 | Panel 1 | [MGAS-062] on services panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1 | [MGFP-002] on services panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | MSP | MGFP-041 | FLOWMETER: oxygen | 2 | 1 | Panel 1 | [MGFP-004] on services panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026] patient services
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] 1 to clock
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-106 | GPO: single, ceiling mounted | 3 | 1 |  | [ELGP-101] 1 to laser positioning light
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | [ELGP-123.1]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-226 | GPO: double, in floor box | 4 | 1 |  | [ELGP-203]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | [ELGP-223] to walls
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ELPR-031 | PANEL: UPS status indicator, wall mounted | 1 | 1 |  | [ELPR-007] on service panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | [ELPR-006] on services panel
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | [ELBO-012] number determined by number of doors
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] on services panel + indicator button & light
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] on services panel + indicator button & light
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ITIN-011 | OUTLET: data, single RJ45, ceiling mounted | 2 | 1 |  | [ITIN-011]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3 | 1 |  | [ITIN-016]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | [ITIN-026] on wall near PET-CT unit
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ITIN-162 | FLOOR BOX: power and data outlets, flush floor mounted | 2 | 1 |  | [ITIN-143]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ITSE-166 | INTERCOM: audio, slave, wall mounted | 1 | 1 |  | [ITSE-029] handsfree to control room
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | ITSE-297 | BUTTON: door release, remote activation, wall mounted | 1 | 1 |  | [ITSE-025]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | LIFX-192 | LIGHT: feature, backlit panels, ceiling mounted | 2 | 1 |  | [LIFX-038]
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | LIFX-213 | LIGHT: illuminated sign, x-ray in use | 2 | 1 |  | [LIFX-002] to outside of all doors to room, auto on when modality is in use, vendor to provide signal wiring to light
PET-CT | PET-CT Imaging Room | Nuclear Medicine / PET | SER | MEGE-001 | CONTROL PANEL: HVAC | 1 | 1 |  | [MEGE-007] alarm for temperature range