## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | Translation and QA Only | 4 | 2700 |  | 1 | 07.04.2026 |  | 8am to 6pm, daily (may vary depending on service requirements) | 1 staff | The Dispensing Workstation provides workspace to prepare, assemble and label patient medications for dispensing to inpatients and outpatients. The workstations can be configured to provide dispensing/assembly stations and a checking station as required. | ~ Dispensing workstations should be arranged to support effective workflows, reduce travel time and avoid error. These stations should be arranged such that extended reaches are avoided. Where dispensing workstations are arranged adjacent to each other, corridors in between them should be wide enough to provide unobstructed movement for staff and trolleys. ~ Ready access to the bulk store and refrigerated storage is required. ~ Printer and telephone facilities to be shared between multiple workstations. A Multifunction device is to be in close proximity to the dispensing area. ~ Ensure adequate lighting over workspace - task lighting may be required. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | [CLCN-009]
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FIN | CLTI-022.02 | CEILING: drop-in tiles, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | [CLTI-002]
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 2 | 1 |  | [ELGP-223] extent of emergency power to be determined based on service requirements
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FFE | FQBS-172 | CHAIR: office, ergonomic, high | 1 | 1 |  | [FQBS-019]
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] quantity and type of bins to be based on local waste management policies
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FFE | FQWS-212 | BIN: confidential document, secure, 30L | 1 | 1 |  | [FQCW-064] quantity and type of bins to be based on local waste management policies
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | [ITIN-026]
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FFE | ITNE-101 | COMPUTER: single display screen, central processing unit (CPU), keyboard and mouse, desktop | 1 | 1 |  | [ITNE-007] may be on desk mounted bracket
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FFE | ITNE-171 | DISPLAY SCREEN: computer | 1 | 3 |  | [ITNE-063] optional, depending on project ICT requirements; may be on desk mounted bracket
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FFE | ITNE-221 | INPUT DEVICE: bar code scanner | 1 | 1 |  | [ITNE-003]
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FFE | ITNE-316 | PRINTER: labels, small, desktop | 1 | 1 |  | [FQGE-093]
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FFE | MMPH-081 | WORKSTATION SYSTEM: pharmacy, shelving, with integral power and data, softwired | 1 | 1 |  | [FQDW-048 + FQDW-047] services spine may be shared between multiple workstations
PHA-DS | Pharmacy - Dispensing Workstation | Pharmacy | FFE | MMPH-174.01 | WORKSTATION: pharmacy, straight, adjustable height, 900H nom, 750D x 1800W | 1 | 1 |  | [FQDW-046]