## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | Translation and QA Only | 12 | 2700 | PREP | 4 | 07.04.2026 |  | 8am to 6pm, daily (may vary depending on service requirements) | 1-2 staff | The Preparation Room provides a dedicated area for the extemporaneous preparation and compounding of non-aseptically prepared products and cleaning of equipment as required. The Preparation Room should be located in close proximity to the dispensing area. |  | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of mobile equipment in adjacent area; to be coordinated with corridor wall protection
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | [DWGL-003]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | SER | ELGP-201 | GPO: double, wall mounted | 4 | 1 |  | [ELGP-208] provision of emergency power to be determined based on service requirements
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | SER | ELSW-001 | SWITCH: light | 3 | 1 |  | [ELBO-015] 1 x general room lighting, 2 x task lights
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 11 | 1 | Floor Skirting | [FLSK-010]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-044]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | FQWS-053 | BIN: general waste, 50L | 1 | 1 |  | [FQCW-019] quantity and type of bins to be based on local waste management policies
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | FQWS-273 | BIN: pharmaceutical waste, 50L | 1 | 1 |  | [FQCW-065] quantity and type of bins to be based on local waste management policies
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | [HYBA-010]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | HYBA-303 | SINK: single bowl, with drainer | 1 | 1 |  | [HYBA-069]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037] to basin
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | HYTP-152 | TAPWARE: sink, mixer, fixture mounted, accessible | 1 | 1 |  | [HYTP-040]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-020] may be height adjustable item depending on service requirements
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | JOBE-031 | BENCH: 600D, laminate | 2 | 1 |  | [FIJO-059]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | JOCU-103 | CUPBOARD: wall mounted, single door, glazed | 1 | 1 |  | [FIJO-159]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | JOCU-123 | CUPBOARD: wall mounted, double door, glazed | 3 | 1 |  | [FIJO-148]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | JOCU-201 | CUPBOARD: under bench, single door | 1 | 1 |  | [FIJO-141]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | JOCU-221 | CUPBOARD: under bench, double door | 3 | 1 |  | [FIJO-136]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | JOGE-001 | BULKHEAD: joinery | 2 | 1 |  | [FIJO-212]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | SER | LIFX-108 | LIGHT: task, integral to joinery | 2 | 1 |  | [LIFX-008] under wall mounted joinery
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | MMGE-201 | SCALES: digital, benchtop | 2 | 1 |  | [MMGE-185]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | MMLA-172 | CABINET: fume hood, mobile | 1 | 1 |  | [MEEX-013]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FFE | MMTR-004.02 | TROLLEY: stainless steel, 900W x 490D x 900H nom, 2 tier | 1 | 3 |  | [FQSM-016] optional
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 6 | 1 | Wall Finish 2 | [WLWA-020]
PHA-PR | Pharmacy - Preparation Room, Non-Aseptic | Pharmacy | FIN | WLFI-101 | SPLASHBACK: vinyl | 4 | 1 | Wall Finish 3 | [WLWA-010]