## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
PLNT-WT | Plant - Water Treatment | Renal Dialysis | Translation and QA Only | 18 | 2700 | WTPL | 4 | 07.04.2026 |  | 24 hours | 1-2 staff | The Plant - Water Treatment is a lockable room for water treatment systems, including particle filters, water softeners, carbon filters and reverse osmosis (RO) water plant/systems, for the provision of safe water for patients receiving haemodialysis therapy. | ~ The Water Treatment Plant Room should be located in close proximity to the Renal Dialysis Unit to permit short tubing runs to each Treatment Bay, and permit staff to monitor and service the water treatment systems. ~ Refer to manufacturer's specifications for details of RO water treatment plant equipment. In particular, this equipment will incorporate a heat disinfection function, and water saving features. The final components of the system will be determined by the quality of feed water and the ability of the overall system to produce and maintain appropriate water quality. Water treatment requirements to be confirmed by a dialysis water treatment specialist. ~ High level sound isolation is required to ensure noise generated from this room does not invade treatment spaces. ~ Structural engineer's assessment must be sought for floor load bearing capacity with respect to water treatment and pre-treatment plant equipment. ~ Ventilation, exhaust and/or air-conditioning must be designed to accommodate the heat loads of the specified equipment. ~ Light is to be minimised; there are to be no windows provided. ~ Service access will be required around the perimeter of plant equipment, clearances will be determined by manufacturer's specifications. ~ A second door may be provided for separate deliveries and maintenance access if located in the patient treatment area. ~ Pipework and components installed after the water inlet in this room shall not contain brass or copper. ~ Options for cooling of high temperature (circa 90°C) waste water discharged from RO plant is to be considered. ~ Where chilled water is not available, a chiller may be required outside the plant room. The maximum temperature of the feed water to be assessed to allow determination of any requirement for a heat exchanger or chiller design as determined by expert. The intent of this is ensure the temperature at the dialysis point for patient care is between 30-37°C. ~ Redundancy within the pre-treatment and treatment devices/filters should be considered based on the hospitals service criticality level, the feed water quality or risk around quality, and the hospital location where supply of replacement equipment is difficult. | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
PLNT-WT | Plant - Water Treatment | Renal Dialysis | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
PLNT-WT | Plant - Water Treatment | Renal Dialysis | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to room side
PLNT-WT | Plant - Water Treatment | Renal Dialysis | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of mobile equipment in adjacent area; to be coordinated with corridor wall protection
PLNT-WT | Plant - Water Treatment | Renal Dialysis | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | [DWPR-005] to corridor side, extent dependent on movement of mobile equipment in adjacent area; to be coordinated with corridor wall protection
PLNT-WT | Plant - Water Treatment | Renal Dialysis | D+W | AFDPR-051.03 | DOOR FRAME PROTECTION: corners, to 1200H | 1 | 1 | Internal - Door 2 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
PLNT-WT | Plant - Water Treatment | Renal Dialysis | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
PLNT-WT | Plant - Water Treatment | Renal Dialysis | D+W | DOHI-106 | DOOR: hinged, 1 1/2 leaves, 1600 clear opening, solid | 1 | 1 | Internal - Door 1 | [DWSC-027] lockable
PLNT-WT | Plant - Water Treatment | Renal Dialysis | D+W | DOHI-106 | DOOR: hinged, 1 1/2 leaves, 1600 clear opening, solid | 1 | 3 | Internal - Door 2 | [DWSC-027] optional secondary access door, lockable
PLNT-WT | Plant - Water Treatment | Renal Dialysis | FFE | FQBS-202 | STOOL: clinical areas, mobile | 1 | 3 |  | [FQBS-051] optional
PLNT-WT | Plant - Water Treatment | Renal Dialysis | FFE | FQDW-131.03 | WORKSTATION: straight, adjustable height, 720H nom, 600D x 1500W | 1 | 3 |  | [FQDW-051] optional
PLNT-WT | Plant - Water Treatment | Renal Dialysis | FFE | FQGE-442 | PALLET: half size | 1 | 1 |  | [FQSN-138]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-009]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | FIN | CLFS-013 | CEILING: flush set, suspended, moisture resistant | 1 | 1 | Ceiling Finish 1 | [CLFS-009]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | FIN | FLGE-003 | FLOOR FINISH: concrete, trowel finished, sealed | 1 | 1 | Floor Finish 2 | [FLGE-003]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | FIN | FLSK-081 | SKIRTING: concrete, sealed, coved | 6 | 1 | Floor Skirting | [FLSK-002]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | ELGP-131.01 | GPO: single, emergency power, wall mounted, horizontal | 1 | 3 |  | [ELGP-123] optional, dependent on equipment
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | ELGP-231.01 | GPO: double, emergency power, wall mounted, horizontal | 8 | 1 |  | [ELGP-223] for water treatment equipment, high level (power tools to be on a separate circuit)
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | ELSW-001 | SWITCH: light | 1 | 3 |  | [ELBO-010] optional
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | ELSW-001 | SWITCH: light | 1 | 1 |  | [ELBO-015]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYDR-021 | DRAIN: floor waste, round | 1 | 1 |  | [HYDR-004] floor waste must be capable of handling high flow rates and high temperature water (up to 90°C) from the RO water plant
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYDR-037 | DRAIN: floor waste, sump, square | 1 | 1 |  | [HYDR-017] floor waste must be capable of handling high flow rates and high temperature water (up to 90°C) from the RO water plant
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYDR-101 | TUNDISH: fixture mounted | 2 | 1 |  | [HYDR-006]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYDR-102 | TUNDISH: floor mounted | 1 | 1 |  | [HYDR-018] tundish must be capable of handling high flow rates and high temperature water (up to 90°C) from the RO water plant
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYGE-181 | VALVE: backflow prevention, wall recessed | 1 | 1 |  | [HYGE-028]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYGE-211 | PLANT: water treatment, softener tank | 1 | 1 |  | [HYGE-024] size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYGE-212 | PLANT: water treatment, brine tank | 1 | 1 |  | [HYGE-019] size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYGE-213 | PLANT: water treatment, multimedia tank | 1 | 1 |  | [HYGE-021] size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYGE-221 | PLANT: water treatment, carbon filter | 3 | 3 |  | [HYGE-020] 1 is optional; size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYGE-222 | PLANT: water treatment, ultraviolet filter | 1 | 1 |  | [HYGE-027]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYGE-231 | PLANT: water treatment, particle filter, 1 micron | 1 | 1 |  | [HYGE-022] size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYGE-232 | PLANT: water treatment, particle filter, 5 micron | 1 | 1 |  | [HYGE-023] size/quantity based on feed water quality and confirmed by a dialysis water pre-treatment expert
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYGE-251 | PLANT: dialysis, water treatment, reverse osmosis | 1 | 1 |  | [HYGE-012] details according to manufacturer's specifications
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYGE-301 | PUMP: pressure booster | 2 | 1 |  | [HYGE-016] to suit water pressure drop through pre-filtration train where building water pressure and flow is inadequate
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | HYTP-431 | OUTLET: water, cold | 1 | 1 |  | [HYTP-008]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | ITBU-376 | ALARM: chlorine detector | 1 | 3 |  | [ITBU-024] optional, dependent on local operational policies
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | ITBU-402 | ALARM: equipment monitoring, water treatment malfunction | 1 | 1 |  | [ITBU-002] connected to BMS and staff station in unit
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | [ITIN-026]
PLNT-WT | Plant - Water Treatment | Renal Dialysis | SER | MEGE-201 | PLANT: heat exchanger, supplied by mechanical chilled water | 1 | 1 |  | [MEGE-010] as required; may be necessary to cool feed water where high temperatures are expected, refer to technical expert for required outlet temperature (generally <25°C)