## RDS
Standard Components - Room Data Sheet
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Description
|  |  | Briefing |  |  |  | Description or Special Requirements
|  |  | Remarks | Occupancy | Hours of Operation | Acoustics
AusHFG Room Code | Room Name | Prog. Area | (Multi line edit) | (Single line edit) | (Single line edit) | (Single line edit) | (Formatted text)
PODTR-12 | Podiatry Treatment, 12m2 | 12 |  | 1 patient; 1 staff | Available 24 Hours | Sound attenuation level high, Acoustic privacy is required. | The Podiatry Treatment room provides for podiatry consultation, examination and treatment. The room may be used for measuring and fitting prosthetic appliances but not for fabrication. An external outlook is desirable. Acoustics: sound attenuation level high; Acoustic privacy is required Body Protected electrical area

## Items in Room
Standard Components - Items in Room
1st March 2016
Generated by dRofus (C) dRofus Pty Ltd
Items | [6 empty] | Fabrics |  |  | Service allocations
Connections
[7 empty] | Material | Finish | Specification | Ele | Data | CdW | HtW | Tap | WmW | Dns | Gas | Stm
AusHFG Room Code | Room Name | Item list | BIM ID | Name | Gross quantity | Comment | (Single line edit) | (Single line edit) | (Single line edit) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field) | (Logic field)
PODTR-12 | Podiatry Treatment, 12m2 | FE | FE-11400 | Computer - PC & monitor | 1 | flat screen |  |  |  | Yes | Yes | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FE | FE-2800 | Basin - handwash, Type B | 1 | refer to BHWS-B (sim) |  |  |  | No | No | Yes | No | Yes | Yes | Yes | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FE | FE-40300 | Plaster trap | 1 | under sink |  |  |  | No | No | No | No | No | No | Yes | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FE | FE-40458 | Chair - podiatry, electric | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FE | FE-43800 | Refrigerator - under-bench, 120 Litre | 1 | optional |  |  |  | Yes | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FE | FE-47890 | Sink & drainer - single, 930mmL | 1 | provide warm water |  |  |  | No | No | Yes | Yes | Yes | Yes | Yes | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FE | FE-54510 | Telephone - handset, standard | 1 |  |  |  |  | No | Yes | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FE | FE-68600 | Xray viewer - 1 screen | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FE | FE-5857 | Light - procedures small, ceiling | 1 |  |  |  |  | Yes | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FE | FE-4045 | Tapware - elbow mixer | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FF | FF-1050 | Bench - laminate | 1 | open under part for write-up area |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FF | FF-1250 | Blind - Venetian | 1 | to external window if provided |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FF | FF-12900 | Wire panel - for storage-bins | 1 | above bench, optional |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FF | FF-21680 | Stool - adjustable, mobile | 1 | for staff |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FF | FF-21755 | Storage bins | 3 | for louvred panel, optional |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FF | FF-24400 | Whiteboard | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FF | FF-4410 | Cupboard - under bench | 1 | under part bench |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FF | FF-4420 | Cupboard - under bench, lockable | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FF | FF-4470 | Cupboard - wall mounted, lockable | 2 | over bench, adjustable shelves |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FF | FF-4470 | Cupboard - wall mounted, lockable | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FF | FF-6152 | Dispenser - disposable glove | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FF | FF-6154 | Dispenser - paper/ hand towel | 2 | to basin & sink |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FF | FF-6156 | Dispenser - soap | 2 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FF | FF-6158 | Dispenser - soap antiseptic | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FF | FF-6163 | Dispenser - mask | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FF | FF-7402 | Trolley - equipment | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | FF | FF-5824 | Waste bin - general | 1 | to basin |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | SE | S-9000 | GPO: Single | 2 | fridge, XRV |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | SE | S-9001 | GPO: Double | 3 |  |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | SE | S-9040 | Body protected | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | SE | S-9060 | GPO: Special: for equipment | 1 | Podiatry chair |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | SE | S-1006 | Voice / Data outlet: double | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | SE | S-5000 | Airconditioning | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | SE | S-6000 | General fluorescent | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | SE | S-6200 | Light switches | 2 |  |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | SE | S-6055 | Special: task light, built in | 2 | under O/H cupboards |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | SE | S-8080 | Emergency call | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | SE | S-1951 | Staff assist call | 1 |  |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | Fabrics | 1000 | Floor finish | 1 |  | Vinyl | Standard slip resistant | Seamless, coved | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | Fabrics | 3000 | Wall finish | 1 |  | Paint | Acrylic, washable |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | Fabrics | 3060 | Wall finish | 1 | to basin & sink; Default = vinyl; tiles also acceptable | Vinyl | Prefinished | Splashback | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | Fabrics | 5060 | Ceiling - Acoustic | 1 | Default = acoustic tiles; flush set plasterboard ceiling also acceptable | Acoustic | Prefinished | Drop-in tiles, 600x1200 | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | Fabrics | 8010 | Door protection | 1 | Equal to Acrovyn | Composite | Prefinished PVC | Protection plate to 900 AFFL | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | Fabrics | 8040 | Door protection | 1 | Equal to Acrovyn | Composite | Prefinished PVC | To door frame | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | Fabrics | 9128 | Door - 1200mm | 1 | 910/1400mm clear opening, half door optional | Solid Core/ Glass | Paint | 1 1/2 leaf, observation panel | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | Fabrics | 7001 | Windows | 1 | desirable |  |  |  | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | Fabrics | 6030 | Cornice | 1 |  | Aluminium | Powdercoat | 24mm shadow angle | No | No | No | No | No | No | No | No | No
PODTR-12 | Podiatry Treatment, 12m2 | Fabrics | 2000 | Skirting | 1 |  | Vinyl | Prefinished | Floor vinyl coved, 150 mmH | No | No | No | No | No | No | No | No | No