## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
PROC | Procedure Room | Ambulatory Care | Translation and QA Only | 20 | 3000 | PROC-20 | 6 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient;; up to 4 staff | The Procedure Room provides a controlled environment and facilities for carrying out procedures that do not require the full facilities of the Operating Suite. This may include suturing of wounds, complex dressings, lumbar puncture, catheterisations. administration of local anaesthesia and use of medical gases in connection with the procedures being performed. General anaesthesia will not be administered in this room. | ~ Lead shielding may be required depending on use of mobile imaging equipment. Treatment of bariatric patients including mobile, bariatric lifter access. ~ The ceiling height has been nominally shown at 3000mm, however 2700mm is also acceptable and the height is to be determined based on ceiling mounted equipment and operational requirements. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
PROC | Procedure Room | Ambulatory Care | D+W | AFDPR-056.03 | DOOR FRAME PROTECTION: full wrap, to 1200H | 1 | 3 | Internal - Door 1 | [DWPR-010] optional, provision and extent dependent on frame material/finish and movement of beds and mobile equipment in adjacent area
PROC | Procedure Room | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to corridor side, extent dependent on movement of beds and mobile equipment in adjacent area; to be coordinated with corridor wall protection
PROC | Procedure Room | Ambulatory Care | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 1 | [DWPR-005] to room side
PROC | Procedure Room | Ambulatory Care | D+W | DOHI-114.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, standard vision panel | 1 | 1 | Internal - Door 1 | DWGL-033]
PROC | Procedure Room | Ambulatory Care | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
PROC | Procedure Room | Ambulatory Care | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | [FIDI-025] to basin
PROC | Procedure Room | Ambulatory Care | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | [FIDI-001]
PROC | Procedure Room | Ambulatory Care | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | [FIDI-030] to basin
PROC | Procedure Room | Ambulatory Care | FFE | FIDI-261 | DISPENSER: soap, antimicrobial, wall mounted | 1 | 1 |  | [FIDI-031] to basin
PROC | Procedure Room | Ambulatory Care | FFE | FIHR-026 | HOOK: coat, wall mounted | 2 | 3 |  | [FIHR-026] optional
PROC | Procedure Room | Ambulatory Care | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1 |  | [FIHR-019] quantity to suit number of suction outlets
PROC | Procedure Room | Ambulatory Care | FFE | FIHR-111 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | [FIHR-016]
PROC | Procedure Room | Ambulatory Care | FFE | FIHR-411 | BRACKET: patient monitor, articulated, wall mounted | 1 | 3 |  | [FIHR-011] optional, for cardiac/vital signs monitor
PROC | Procedure Room | Ambulatory Care | FFE | FQBS-203 | STOOL: clinical areas, mobile, high | 1 | 1 |  | [FQBS-052]
PROC | Procedure Room | Ambulatory Care | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | [FQGE-010]
PROC | Procedure Room | Ambulatory Care | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | [FQCW-043]
PROC | Procedure Room | Ambulatory Care | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | [FQCW-016] to basin
PROC | Procedure Room | Ambulatory Care | FFE | FQWS-233 | BIN: clinical waste, 50L | 1 | 3 |  | [FQCW-008] optional; type, size and quantity of bins to be determined based on service requirements and waste management policies
PROC | Procedure Room | Ambulatory Care | FFE | HYBA-101 | BASIN: type A, handwashing | 1 | 1 |  | [HYBA-009]
PROC | Procedure Room | Ambulatory Care | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | [HYTP-037]
PROC | Procedure Room | Ambulatory Care | FFE | ITBU-441 | CLOCK: analogue display, electric, wall mounted | 1 | 1 |  | [ITCL-014]
PROC | Procedure Room | Ambulatory Care | FFE | ITNE-076 | TELEPHONE: handset, wall mounted | 1 | 1 |  | [ITNE-053]
PROC | Procedure Room | Ambulatory Care | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | [ITNE-008+MMGE-164] computer may alternatively be on benchtop or wall mounted; allocation of WOWs across department to be rationalised
PROC | Procedure Room | Ambulatory Care | FFE | ITNE-311 | PRINTER: desktop | 1 | 3 |  | [ITNE-023] optional
PROC | Procedure Room | Ambulatory Care | FFE | JOBE-031 | BENCH: 600D, laminate | 1 | 1 |  | [FIJO-059]
PROC | Procedure Room | Ambulatory Care | FFE | JOCU-221 | CUPBOARD: under bench, double door | 1 | 1 |  | [FIJO-135]
PROC | Procedure Room | Ambulatory Care | FFE | JOGE-001 | BULKHEAD: joinery | 1 | 1 |  | [FIJO-212] plasterboard bulkhead also acceptable
PROC | Procedure Room | Ambulatory Care | FFE | JOSH-101 | SHELF UNIT: wall mounted, adjustable shelves | 1 | 1 |  | [FIJO-152]
PROC | Procedure Room | Ambulatory Care | FFE | LIFX-121 | LIGHT: procedure, minor, single articulated arm, 1 light head, ceiling mounted | 1 | 1 |  | [LIFX-013]
PROC | Procedure Room | Ambulatory Care | FFE | MMBE-156 | TROLLEY: patient, examination | 1 | 1 |  | [MMBE-043]
PROC | Procedure Room | Ambulatory Care | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1 |  | [MMGE-100] quantity to suit number of suction outlets
PROC | Procedure Room | Ambulatory Care | FFE | MMGE-233 | DIAGNOSTIC SET: otoscope and ophthalmoscope, wall mounted | 1 | 3 |  | [MMGE-031] optional, may be portable/mobile on stand
PROC | Procedure Room | Ambulatory Care | FFE | MMPM-021 | MONITOR: patient, high acuity | 1 | 3 |  | [MMHA-008] optional
PROC | Procedure Room | Ambulatory Care | FFE | MMTR-071 | TROLLEY: equipment, 490W x 490D x 900H nom | 1 | 1 |  | [MMGE-119]
PROC | Procedure Room | Ambulatory Care | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-032]
PROC | Procedure Room | Ambulatory Care | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
PROC | Procedure Room | Ambulatory Care | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
PROC | Procedure Room | Ambulatory Care | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006]
PROC | Procedure Room | Ambulatory Care | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 7 | 1 | Floor Skirting | [FLSK-010]
PROC | Procedure Room | Ambulatory Care | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007] floor finish must be minimum slip rating R10 / Pendulum P3 or agreed equivalent to extend under basin or inset section of non-slip vinyl required
PROC | Procedure Room | Ambulatory Care | FIN | WLFI-001 | WALL FINISH: paint | 4 | 1 | Wall Finish 1 | [WLWA-004]
PROC | Procedure Room | Ambulatory Care | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 4 | 1 | Wall Finish 2 | [WLWA-020]
PROC | Procedure Room | Ambulatory Care | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | [WLWA-007] to basin
PROC | Procedure Room | Ambulatory Care | MSP | ELGP-116 | GPO: single, on services panel | 3 | 1 | Panel 1 | [ELGP-105]
PROC | Procedure Room | Ambulatory Care | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 3 | 1 | Panel 1 | [ELGP-122]
PROC | Procedure Room | Ambulatory Care | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1 | [ITIN-025]
PROC | Procedure Room | Ambulatory Care | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1 | [MGAS-022]
PROC | Procedure Room | Ambulatory Care | MSP | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | 3 | Panel 1 | [MGAS-032] optional, dependent on service requirements
PROC | Procedure Room | Ambulatory Care | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042] quantity dependent on service requirements
PROC | Procedure Room | Ambulatory Care | MSP | MGAS-052 | OUTLET: scavenge, on services panel | 1 | 3 | Panel 1 | [MGAS-053] optional, dependent on service requirements, provide if nitrous oxide required
PROC | Procedure Room | Ambulatory Care | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1 | [MGAS-062] quantity dependent on service requirements
PROC | Procedure Room | Ambulatory Care | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1 | [MGFP-002]
PROC | Procedure Room | Ambulatory Care | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004] quantity to suit number of oxygen outlets
PROC | Procedure Room | Ambulatory Care | MSP | MGFP-082 | BLENDER: oxygen (O2) and nitrous oxide (N20) | 1 | 3 | Panel 1 | [MMMA-011] optional, may be mobile, on trolley or wall mounted
PROC | Procedure Room | Ambulatory Care | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
PROC | Procedure Room | Ambulatory Care | MSP | MGFP-061 | ADAPTER: suction | 1 | 3 | Panel 1 | [MMGE-002] 1 is optional, quantity to suit number of suction outlets
PROC | Procedure Room | Ambulatory Care | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 1 | [ITCL-006] + indicator button & light
PROC | Procedure Room | Ambulatory Care | MSP | ITCL-183 | BUTTON: nurse call, staff assist, with cancel, on services panel | 1 | 1 | Panel 1 | [ITCL-008] + indicator button & light
PROC | Procedure Room | Ambulatory Care | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1 | [MMGE-002] quantity to suit number of suction outlets
PROC | Procedure Room | Ambulatory Care | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 3 | Panel 1 | [MGAS-062] 1 is optional, quantity dependent on service requirements
PROC | Procedure Room | Ambulatory Care | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 3 | Panel 1 | [MGAS-042] 1 is optional, quantity dependent on service requirements
PROC | Procedure Room | Ambulatory Care | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 3 | Panel 1 | [MGFP-004] 1 is optional, quantity to suit number of oxygen outlets
PROC | Procedure Room | Ambulatory Care | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | [ELGP-110]
PROC | Procedure Room | Ambulatory Care | SER | ELPR-071 | RCD: residual current device, wall mounted | 4 | 1 |  | [ELPR-006]
PROC | Procedure Room | Ambulatory Care | SER | ELSW-001 | SWITCH: light | 3 | 1 |  | [ELBO-015] 1 x general room lighting, 1 x task light, 1 x examination light
PROC | Procedure Room | Ambulatory Care | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] + indicator button & light
PROC | Procedure Room | Ambulatory Care | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | [ITCL-028] call button on the handset
PROC | Procedure Room | Ambulatory Care | SER | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | 3 |  | [ITIN-016] 1 to telephone, 1 - optional, for cardiac/vital signs monitor
PROC | Procedure Room | Ambulatory Care | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 |  | [ITIN-026]
PROC | Procedure Room | Ambulatory Care | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1 |  | [ITSE-006]
PROC | Procedure Room | Ambulatory Care | SER | LIFX-108 | LIGHT: task, integral to joinery | 1 | 1 |  | [LIFX-008]
PROC | Procedure Room | Ambulatory Care | SER | HYDR-201 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
PROC | Procedure Room | Ambulatory Care | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin tapware
PROC | Procedure Room | Ambulatory Care | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin tapware
PROC | Procedure Room | Ambulatory Care | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside door
PROC | Procedure Room | Ambulatory Care | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] low level, for patient trolley
PROC | Procedure Room | Ambulatory Care | SER | ELGP-106 | GPO: single, ceiling mounted | 1 | 1 |  | [ELGP-101] to procedure light
PROC | Procedure Room | Ambulatory Care | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 3 |  | [ELGP-123] optional, for cardiac/vital signs monitor
PROC | Procedure Room | Ambulatory Care | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208]