## Room Template Data
Room Data Sheet - File for Import
2026-04-07
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Panorama - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | Translation and QA Only | 9 | 2700 | PBTR-H-9 | 7 | 07.04.2026 |  | Up to 24 hours (dependent on unit operating hours) | 1 patient; 1 visitor; 1-2 staff intermittently | A Patient Bay - Holding provides facilities for patient holding and preparation prior to examination, diagnostic imaging, treatment, procedures or surgery. | ~ A handwashing basin will be provided close by to be shared between multiple bays. ~ Staff observation is required and, where possible, a clear line of sight from a staff station is to be provided. Close access to a patient toilet is required. ~ The configuration of the Medical Services Panel (MSP), including medical gases, power and data, will be dependent on service requirements. Data provision is to take into consideration the increasing demand and sophistication of information systems and the technological development of monitoring equipment. ~ The requirement for fixed wall mounted patient monitoring will be dependent on service requirements. A patient monitor may be located on the left or right side of bedhead depending on monitor functionality and staff workflows. Appropriate wall supports are required for mounting the bracket where a monitor is provided. ~ Where patient monitoring is provided, criticality of monitoring is to be assessed. Provision of emergency/standby power or UPS is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Facilities to accommodate bariatric patients within a select number of bays, including accommodating bariatric beds, is to be considered to ensure sufficient amenity is provided. Provision will be dependent on service and patient cohort requirements. ~ Patient transfer aids such as mobile hoists, patient slides and hover mats are to be considered for assisted patient transfers to and from beds in holding bays. A ceiling mounted hoist may also be considered for patient transfers. Selection of transfer aids will be dependent on service and patient cohort requirements as well as WHS risk assessment. Appropriate ceiling support is required for the provision of a ceiling mounted hoist. ~ Depending on service requirements, enclosed holding bays may be provided. Where a Patient Bay is to be enclosed, additional area is required to accommodate a dedicated handwashing basin and circulation at the door. Observation windows may be required and the extent of glazing to be provided is to suit requirements for staff supervision. ~ PPE may be consolidated between multiple bays. Provision of PPE and placement throughout the overall department will be dependent on local infection control policies. ~ A mobile sharps bin will be shared between multiple bays as required. Where use of sharps is frequent, a wall mounted bin sharps bin may be considered. ~ Electronic Medical Record (EMR) management may be performed on a wirelessly connected workstation on wheels (WOW) that is shared between a number of bays. Ensure circulation space is sufficient for bedside and bed end data entry. Parking for WOWs and facilities for battery charging are required to support this model of care. Alternative configurations, such as wall mounted monitors in bays, may be considered depending on local ICT policies. ~ Patient entertainment systems may be considered depending on anticipated length of stay within the holding bay and patient cohort requirements (e.g. paediatrics). Solutions may include individual systems provided to each bay (with integration to patient handset for audio and content control), a central display screen visible from multiple bays, or portable solutions, such as tablets, brought to patients as needed. ~ Operational models for handling patient belongings are to be considered. Close proximity to patient lockers or other secure property storage may be required where belongings are not to be kept with the patient. ~ Depending on anticipated length of stay and pre-procedure requirements, local control of lighting within the bay may be provided to allow patients to dim/adjust lighting level to increase comfort. ~ Access to natural light is required and an external outlook is recommended. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## Items In Room Template
Room Data Sheet - File for Import
2026-04-07
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | [FIDI-014]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | FIDI-247 | HOLDER: alcohol-based hand rub, bed mounted | 1 | 1 |  | [FIHR-068]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1 |  | [FIHR-019]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | [FIHR-033] type and extent of storage dependant on operational policies for stock centralisation/decanting and infection prevention and control policies
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | [FIRT-047]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 3 |  | [FQBS-030] optional
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | [FQGE-010]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 4 | 1 |  | [FQSN-006] type and size of bins dependant on items to be stored
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | [ITNE-008+MMGE-164] shared between multiple bays
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | MMBE-091 | CHAIR: patient, recliner, clinical, electric | 1 | 1 |  | [MMBE-091]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | MMBE-121 | BED: patient, electric, with mattress, holding/recovery | 1 | 1 |  | [MMBE-007]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1 |  | [MMGE-100]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FIN | CLCN-031 | CORNICE: square set | 1 | 1 | Ceiling Cornice | [CLCN-008]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FIN | CLFI-002 | CEILING FINISH: paint, clinical areas | 1 | 1 | Ceiling Finish 2 | [CLFS-006]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FIN | CLFS-011 | CEILING: flush set, suspended | 1 | 1 | Ceiling Finish 1 | [CLFS-006] acoustic tiles are also acceptable
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting | [FLSK-010]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | [FLVY-007]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FIN | WLFI-001 | WALL FINISH: paint | 1 | 1 | Wall Finish 1 | [WLWA-004]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | FIN | WLPR-001 | WALL PROTECTION: bedhead wall panel, full height | 1 | 1 | Wall Protection | [WLPR-001]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 5 | 1 | Panel 1 | [ELGP-122] type and quantity to suit service requirements
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 2 | 1 | Panel 1 | [ITIN-025] quantity to suit service requirements
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1 | [MGAS-022]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1 | [MGAS-042]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1 | [MGAS-062]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1 | [MGFP-002]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1 | [MGFP-004]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1 | [MMGE-002]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | [MMSP-026]
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | [ELGP-109] low, for patient bed
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | [ELGP-208] for patient's own devices
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 3 |  | [ELGP-223] optional, for patient monitoring
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ELPR-071 | RCD: residual current device, wall mounted | 2 | 1 |  | [ELPR-006] to services panel
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ELSW-001 | SWITCH: light | 1 | 3 |  | [ELBO-015] optional, to services panel, for examination downlight if provided
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside curtain
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ITCL-121 | BUTTON: nurse call, patient to staff call, with cancel, wall mounted | 1 | 1 |  | [ITCL-006] on services panel, with indicator button and light
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | [ITCL-008] on services panel, with indicator button and light
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | [ITCL-004] with indicator button and light
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | [ITCL-028] on services panel
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 3 |  | [ITIN-026] optional, for patient monitoring
PT-HOLD-B | Patient Bay - Holding, Bed | Perioperative | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 3 |  | [LIFX-032] optional, provision dependant on service requirements; articulated examination light is also acceptable