## Room Template Data
Patient Bay - Emergency, Acute Treatment, Enclosed (PTB-E-ACU-E) - Room Template Properties and Room Template Data
2025-08-18
No. of Standard Components = 1
Code | Template Name | Standard Area | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Briefing - Hours of Operation - Duration - Duration | Briefing - Hours of Operation - Duration - extended/limited hours | Briefing - Hours of Operation - Hours/days - Open time | Briefing - Hours of Operation - Hours/days - Close time | Briefing - Hours of Operation - Hours/days - Days | Briefing - Hours of Operation - Comment | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experiance system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statuatory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magentic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: sensitive | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | 15 | PRTR-AS | 2 | 18.08.2025 | 24 hours | FALSE |  |  |  |  | 1 patient; 1 visitor; 1-2 staff intermittently | The Patient Bay - Emergency, Acute Treatment, Enclosed provides an enclosed space and the facilities for assessment, treatment and observation of patients with acute conditions and injuries within the Emergency Unit. | ~ This Standard Component shows the requirements for a general enclosed patient bay for acute emergency treatment. Where it is intended for use as a standard isolation room, an ensuite that is not shared with other patients will be required. Where it is intended for use as a negative pressure isolation room, an ensuite that is not shared and an anteroom will be required. A negative pressure room will also have specific air handling and grille location requirements, and these are to be confirmed at project level to suit local engineering services guidance. For the requirements of an open patient bay refer to PTB-E-ACU-E Patient Bay – Emergency, Acute Treatment ~ The extent of glazing is to be determined at project level to suit the overall department layout and requirements for patient observation. Provision of integral blinds or extension of the privacy curtain track over the internal window is to be determined to suit requirements for observation and patient privacy. ~ Close access to PPE is required between rooms. Refer to Part D: Infection Prevention and Control for more information. ~ A wall clock should be visible from all clinical areas. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ Electronic medical record (EMR) input may be performed on a wirelessly connected workstation on wheels (WOW) that is shared between a number of bays and rationalised across the unit, with quantity to suit clinical service requirements and staffing models. Ensure circulation space is sufficient for bedside and bed-end data entry. Parking areas for WOWs and facilities for battery/equipment charging are required to support this model of care. Alternative configurations, such as wall mounted computers (to individual bays or shared between bays) may be provided depending on clinical service requirements, operational models for medical records and local ICT policies. ~ The location of the patient monitor is to be determined to suit clinical workflows and equipment functionality. Appropriate in-wall support is required for mounting the monitor bracket. ~ The content and configuration of the medical services panel (MSP), including medical gases, power and data, will be dependent on clinical service requirements and is to be confirmed at project level. ~ The clear area required for patient transfer aids such as mobile hoists, patient slides and hover mats, and the staff required to assist/complete the patient transfer, is to be considered for transfers to and from beds. Work health and Safety (WHS) policies and patient transfer devices that are intended to be used in the patient bay should be confirmed at project level. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage of all patient bays is to suit local security and WHS policies and operational service requirements. ~ Provision for the temporary storage of patient property (e.g. wall-mounted baskets, coat hooks, etc.) should be considered for patient and visitor comfort and convenience. ~ A dedicated power outlet, clearly separate from the Medical Services Panel (MSP), is recommended to support patient and visitor use/charging of portable devices. Inclusion of integral USB outlets will depend on local ICT policies. ~ Patient entertainment systems may be considered depending on anticipated length of stay within the patient bay and patient cohort requirements (e.g. paediatrics). Solutions may include individual systems provided to each enclosed patient bay (with integration to patient handset for speaker, and audio/content controls) or portable solutions, such as tablets, brought to patients as needed. ~ Size, type and quantity of waste bins, including sharps bins, will be dependent on clinical service requirements, operational models for waste management and local infection prevention and control (IPC) policies. ~ Provision of emergency/standby power or uninterruptible power supply (UPS) is to be confirmed to suit site and service requirements. Confirmation to be based on risk assessment considering the impact of a power outage on patient care/safety. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. ~ Access to natural light and an external outlook is desirable, and patient privacy must be considered when determining window placement. Where high-level windows are provided to the bedhead wall of enclosed patient bays consideration must be given to the location of wall mounted items such as patient monitors. Window coverings must meet IPC requirements. | TRUE | FALSE | FALSE | TRUE | TRUE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Items In Room Template
Standard Components - Items in Room Template
2025-08-18
No. of Standard Components = 1
Code | Template Name | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | D+W | WIFX-057.04 | WINDOW: fixed, internal, double glazed, sill at 900H, with integral blind | 1 | 1 | Internal - Window 1 | extent of glazing is to be determined at project level to suit the overall department layout and requirements for patient observation; provision of integral blinds or extension of the privacy curtain track over window is to be determined to suit requirements for observation and patient privacy
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | D+W | DOHI-144.01 | DOOR: hinged, 1 1/2 leaves, 1400 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 1 | extent of glazing is to be determined at project level to suit the overall department layout and requirements for patient observation
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 2 | 1 | Internal - Door 1 | to both sides
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 3 | Internal - Door 1 | optional; provision dependent on frame material and finish
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | D+W | DOHI-003.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid | 1 | 1 | Internal - Door 2 | optional; to ensuite if provided
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | D+W | DOHI-043.01 | DOOR: hinged, 1 leaf, 900 clear opening, solid, wide vision panel | 1 | 1 | Internal - Door 3 | optional; to anteroom if provided
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 2 | to patient room side
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 2 | optional; provision dependent on frame material and finish
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | D+W | AFDPR-001.01 | DOOR PROTECTION: kickplate, to 300H | 1 | 1 | Internal - Door 2 | to ensuite side
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | D+W | AFDPR-006.01 | DOOR PROTECTION: plate, to 900H | 1 | 1 | Internal - Door 3 | to both sides
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | D+W | AFDPR-056.01 | DOOR FRAME PROTECTION: full wrap, to 900H | 1 | 1 | Internal - Door 3 | optional; provision dependent on frame material and finish
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1 |  | may alternatively be provided as a bottle in a holder located on the end of the bed
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 2 | 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | FIHR-110 | BRACKET: sharps bin, wall mounted | 1 | 1 |  | sharps bin may alternatively be provided on a dedicated cart or on clinical trolleys that are shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | FIHR-151 | PANEL: storage baskets, wall mounted | 1 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 1 | 1 |  | for the temporary storage of patient property
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | FIHR-297 | BRACKET: combined single screen all-in-one computer, keyboard and mouse, height adjustable, wall mounted | 1 | 1 |  | optional; required if all-in-one computer and display screen is provided
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | FIHR-408 | BRACKET: patient monitor, articulated, wall mounted | 1 | 1 |  | with cable and accessory management items as required
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | FQGE-101 | CURTAIN: privacy screen | 1 | 1 |  | to entry door
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | FQGE-112 | BASKET: storage, for wall mounted panel, small | 3 | 1 |  | type and extent of storage for consumables to suit clinical service requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | FQGE-113 | BASKET: storage, for wall mounted panel, medium | 1 | 1 |  | for the temporary storage of patient property
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | FQTA-091 | TABLE: overbed, mobile, height adjustable | 1 | 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | size to suit clinical requirements and operational models for frequency of disposal; may alternatively be provided on a dedicated cart or on clinical trolleys that are shared across the unit and brought to the patient bay as required; solution to suit clinical service requirements and local IPC policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | size, type, quantity and distribution of waste bins will be dependent on clinical service requirements, operational models for waste management and local IPC policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | size, type, quantity and distribution of waste bins will be dependent on clinical service requirements, operational models for waste management and local IPC policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | ITNE-111 | COMPUTER: workstation on wheels (WOW), medical grade, all-in-one computer, keyboard and mouse, on cart | 1 | 1 |  | shared between multiple patient bays with quantity to be rationalised across the unit to suit clinical service requirements, operational models for electronic medical records, local ICT policies and staffing models
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | ITNE-122 | COMPUTER: single display screen, all-in-one, medical grade | 1 | 1 |  | optional; may be provided in lieu of WOW; provision dependent on clinical service requirements, operational model for electronic medical records and local ICT policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | ITNE-204 | INPUT DEVICE: keyboard and mouse, wireless, medical grade, washable | 1 | 1 |  | optional; required if all-in-one computer and display screen is provided
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | MMBE-111 | BED: patient, electric, with mattress, emergency | 1 | 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | MMGE-191 | CANNISTER: suction bottle | 2 | 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | MMGE-238 | DIAGNOSTIC SET: otoscope, ophthalmoscope and thermometer, wall mounted | 1 | 1 |  | configuration of equipment to be confirmed to suit clinical services requirements
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | MMPM-011 | MONITOR: patient, medium acuity | 1 | 1 |  | configuration of monitoring to be confirmed to suit clinical services requirements
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | FIDI-106 | DISPENSER: PPE, disposable gloves, wall mounted | 1 | 1 |  | collocate with alcohol-based hand rub
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | FIDI-231 | DISPENSER: paper towel, wall mounted | 1 | 1 |  | to basin
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | FIDI-256 | DISPENSER: soap, wall mounted | 1 | 1 |  | to basin
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | FIDI-261 | DISPENSER: soap, antiseptic, wall mounted | 1 | 1 |  | to basin
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | HYBA-121 | BASIN: type B, handwashing | 1 | 1 |  | location of thermostatic mixing valve to be determined based on ability to share with nearby basins
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | HYTP-067 | TAPWARE: basin, tap set, wall mounted, lever handles | 1 | 1 |  | selection of basin and tapware should be coordinated to ensure compatibility
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1 |  | to entry door
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1 | floor finish must be minimum slip rating R10/Pendulum P3 or agreed equivalent to extend under basin or an inset section of non-slip vinyl is required
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FIN | CLCN-011 | CORNICE: shadow angle, prefinished | 1 | 1 | Ceiling Cornice | to be square set if flush set ceiling is provided
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 1 | 1 | Wall Protection
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FIN | CLTI-023.02 | CEILING: drop-in tiles, anti-microbial, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | flush set ceiling is also acceptable
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FIN | WLFI-011.04 | WALL FINISH: vinyl, to 1500 AFFL | 1 | 1 | Wall Finish 2
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | FIN | WLFI-101 | SPLASHBACK: vinyl | 1 | 1 | Wall Finish 3 | to basin
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to patient's right; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 4 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 2
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 2
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 2
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 2
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 3 | 1 | Panel 2
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 2 | may be combined on a single face plate with staff assist call button; placement to ensure quick access by staff
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient's left; content and configuration to be confirmed based on clinical service requirements and medical equipment selection
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1 | to recessed examination light
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | ELGP-105 | GPO: single, wall mounted, cleaner | 1 | 1 |  | as required for distribution across the unit in accordance with AS/NZS 3003
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | to patient monitor
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | for patient and visitor use/charging of portable devices; inclusion of integral USB outlets is dependent on local ICT policies
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | low height, for patient bed and mattress
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; placement to support quick access by staff
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | placement to support quick access by staff
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | with holder and cable management items as required
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 1 |  | light switch located on MSP; light may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | ELSW-021 | SWITCH: light, dimmer | 1 | 1 |  | to general room lights
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | MEEX-041 | GRILLE: exhaust, wall mounted, low level | 1 | 1 |  | optional; if room is to be used for negative pressure isolation, supply and exhaust air locations are to be determined to suit local engineering services guidance
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to diagnostic set
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | optional; required if all-in-one computer and display screen is provided
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside door; placement to ensure visibility along paths of travel
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | optional; required if all-in-one computer and display screen is provided
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 |  | to patient monitor
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | ELGP-231 | GPO: double, emergency power, wall mounted | 1 | 1 |  | to write-up area
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | HYTP-451 | DIRECT CONNECTION: water, cold | 1 | 1 |  | to basin
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | HYTP-453 | DIRECT CONNECTION: water, warm | 1 | 1 |  | to basin
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit final power provisions
PTB-E-ACU-E | Patient Bay - Emergency, Acute Treatment, Enclosed | SER | HYDR-201.01 | DIRECT CONNECTION: wastewater, general | 1 | 1 |  | to basin
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## SC Set for Publish (hidden)
Code
Emergency | CONS-ENT-OP
Emergency | PTB-E-ACU
Emergency | PTB-E-ACU-E
Emergency | PTB-E-AMB
Emergency | PTB-E-AMT
Emergency | PTB-E-NAC
Emergency | PTB-E-RES
Emergency | RECP-E
Emergency | SSTN-E
Emergency | TRIAGE-CO
Emergency | TRIAGE-RM