## Room Template Data
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Website - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | Full AHIA Review | 6.5 | 2700 | PBAT | 3 | 31.03.2026 |  | 24 hours | 1 patient; 1 visitor; 1-2 staff intermittently | The Patient Bay - Emergency, Ambulance Triage provides the space equipment and services for initial assessment and physical examination of patients that have arrived at the Emergency Unit via ambulance. | ~ Clear line of sight to the patient in the patient bay from the ambulance write-up is required for patient observation. Direct access from ambulance write-up, triage and the reception/administration area of the Emergency Unit is required. ~ A handwash basin is to be provided for every 4-6 patient bays. Quantity and location of handwashing basins in relation to the patient bay will be subject to the overall department layout and informed by ensuring reasonable travel distances and ease of access from each patient bay. Close access to dedicated PPE bays shared between patient bays is also required separate to bays for handwashing basins. Refer to Part D: Infection Prevention and Control for more information. ~ A wall clock should be visible from all clinical areas in the Emergency unit. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ The content and configuration of the medical services panel (MSP), including medical gases, power and data, will be dependent on clinical services requirements and the services requirements of selected equipment. Final configuration is to be confirmed at project level. ~ The clear area required on each side of the patient trolley for use of transfer aids (such as mobile hoists, patient slides, hover mats, etc.), the space for the trolley or wheelchair the patient is being transferred to, and the staff required to assist/complete the patient transfer, is to be considered and confirmed at project level. Work Health and Safety (WHS) policies and patient transfer devices that are intended to be used in the patient bay should be confirmed by the project team. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. ~ Size, type and quantity of waste bins provided within the patient bay, including sharps bins, will be dependent on clinical service requirements, operational models for waste management (including separation of waste streams and frequency of waste removal) and local infection prevention and control (IPC) policies. It may be determined that bins for specific waste streams are to be located in a shared area between multiple patient bays and possibly brought to the patient bay as required. ~ Provision and extent of emergency/standby power and/or uninterruptible power supply (UPS) is to be confirmed to suit clinical services requirements and site conditions. Confirmation of power requirements is to be based on risk assessment considering the impact of a power outage on patient care/safety and medical equipment specifications. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. ~ Access to natural light and an external outlook is desirable. However, patient privacy must also be considered when determining window placement. Where high-level windows are provided to the bedhead wall of patient bays consideration must be given to the location of wall mounted items such as patient monitors. ~ The type, materiality and cleaning requirements of window coverings to external windows is to be confirmed at project level to suit local infection prevention and control (IPC) policies and risk assessments. Refer to Part D Section 6.4 for more information. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | TRUE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE

## Items In Room Template
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 31
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | square set cornice acceptable if flush set ceiling is provided
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FIN | CLTI-024.02 | CEILING: drop-in tiles, anti-microbial, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | flush set ceiling is also acceptable
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1 | to ceiling recessed examination light; fixture may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | shared between multiple ambulance triage bays; size to suit clinical services requirements, operational models for frequency of disposal and local IPC policies
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FQWS-031 | CART: sharps bin, clinical | 1 | 1 |  | shared between multiple ambulance triage bays
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | FQWS-231 | BIN: clinical waste, 20L | 1 | 1 |  | shared between multiple ambulance triage bays; size, type, quantity and location of waste bins will be dependent on clinical services requirements, operational models for waste management and local IPC policies
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside curtain at foot of stretcher; location to ensure visibility along paths of travel
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | located to support quick access by staff
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | located to support quick access by staff
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | SER | ITSE-061 | BUTTON: security, duress, fixed, wall mounted | 1 | 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 1 |  | light switch located on MSP; may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 3 | Panel 1 | optional, provision dependent on clinical services requirements and models of care
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 3 | Panel 1 | optional, to medical air outlet if provided
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to patient's right; content and configuration to be confirmed based on clinical services requirements and medical equipment selection
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
PTB-E-AMB | Patient Bay - Emergency, Ambulance Triage | Emergency | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 1 | 1 | Wall Protection