## Room Template Data
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 1
Code | Template Name | Standard Component Set | ICS Translation Status | Standard Area | Modeled Ceiling Height | Previous Code | RDS Rev: Name | RDS Rev Date: Name | Website - URL for Project Use | Briefing - Hours of Operation | Briefing - Occupancy | Briefing - Description | Briefing - Additional Considerations | Performance Requirements - Electrical - PROTECTION: body protected | Performance Requirements - Electrical - PROTECTION: cardiac protected | Performance Requirements - Lighting - LIGHTING: general | Performance Requirements - Lighting - LIGHTING: colour corrected | Performance Requirements - Lighting - LIGHTING: dimmable | Performance Requirements - Lighting - LIGHTING: indirect | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: buttons / handset | Performance Requirements - Nurse Call and Duress - NURSE CALL SYSTEM: annunciator | Performance Requirements - Nurse Call and Duress - DURESS: fixed | Performance Requirements - Nurse Call and Duress - DURESS: wireless coverage | Performance Requirements - Security - ACCESS CONTROL: to door | Performance Requirements - Security - ACCESS CONTROL: to item / joinery | Performance Requirements - Security - INTERCOM: service communications | Performance Requirements - Security - INTERCOM: security and access control | Performance Requirements - Security - CCTV: camera coverage within room | Performance Requirements - Security - INTRUSION DETECTION: door monitoring | Performance Requirements - Security - INTRUSION DETECTION: spatial monitoring | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: patient entertainment system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: visitor experience system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: virtual collaboration system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: clinical support system | Performance Requirements - ICT and Audio Visual - AUDIO VISUAL: digital operating room system | Performance Requirements - Accessibility - AUDIO: hearing augmentation | Performance Requirements - Accessibility - VISUAL: luminance contrast | Performance Requirements - Accessibility - SIGNAGE: accessible, statutory | Performance Requirements - HVAC - AIRCONDITIONING: general | Performance Requirements - HVAC - AIRCONDITIONING: HEPA filtered | Performance Requirements - HVAC - AIRCONDITIONING: positive pressure | Performance Requirements - HVAC - AIRCONDITIONING: negative pressure | Performance Requirements - HVAC - VENTILATION: exhaust | Performance Requirements - HVAC - VENTILATION: supply | Performance Requirements - HVAC - VENTILATION: natural | Performance Requirements - Medical Gas - MEDICAL GAS: general anaesthesia | Performance Requirements - Medical Gas - MEDICAL GAS: special care | Performance Requirements - Medical Gas - MEDICAL GAS: special care, neonatal ventilation | Performance Requirements - Medical Gas - MEDICAL GAS: birthing | Performance Requirements - Hydraulic - WATER: drinking | Performance Requirements - Hydraulic - WATER: specialty | Performance Requirements - Hydraulic - DRAINAGE: sanitary | Performance Requirements - Hydraulic - DRAINAGE: specialty | Performance Requirements - Fire - DETECTION: smoke | Performance Requirements - Fire - DETECTION: heat | Performance Requirements - Shielding - SHIELDING: ionising radiation | Performance Requirements - Shielding - SHIELDING: magnetic and radio frequency | Performance Requirements - Acoustics - SPEECH PRIVACY: not private | Performance Requirements - Acoustics - SPEECH PRIVACY: moderate | Performance Requirements - Acoustics - SPEECH PRIVACY: private | Performance Requirements - Acoustics - SPEECH PRIVACY: confidential | Performance Requirements - Acoustics - NOISE SENSITIVITY: not sensitive | Performance Requirements - Acoustics - NOISE SENSITIVITY: low | Performance Requirements - Acoustics - NOISE SENSITIVITY: medium | Performance Requirements - Acoustics - NOISE SENSITIVITY: high | Performance Requirements - Acoustics - NOISE GENERATION: low | Performance Requirements - Acoustics - NOISE GENERATION: moderate | Performance Requirements - Acoustics - NOISE GENERATION: high | Performance Requirements - Acoustics - NOISE GENERATION: very high
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | Full AHIA Review | 6.5 | 2700 | PBTR-FT | 3 | 31.03.2026 | https://healthfacilityguidelines.com.au/component/patient-bay-emergency-ambulatory-treatment/?fullscreen=true&utm_source=project-link&rev=3 | 24 hours | 1 patient; 1 visitor; 1-2 staff intermittently | The Patient Bay - Emergency, Ambulatory Treatment (also referred to as “Fast Track”) provides the space equipment and services for assessment, treatment and observation of ambulant patients with non-complex (e.g. single system) acute conditions and injuries requiring a short episode of care within the Emergency Unit. | ~ Clear line of sight to the patient in the patient bay from a staff station/write-up area is required for patient observation. ~ A handwash basin is to be provided for every 4-6 patient bays. Quantity and location of handwashing basins in relation to the patient bay will be subject to the overall department layout and informed by ensuring reasonable travel distances and ease of access from each patient bay. Close access to dedicated PPE bays shared between patient bays is also required separate to bays for handwashing basins. Refer to Part D: Infection Prevention and Control for more information. ~ A wall clock should be visible from all clinical areas in the Emergency unit. The location and type of clocks provided, including any required connection to a master clock system, is to be determined at a project level. ~ The content and configuration of the medical services panel (MSP), including medical gases, power and data, will be dependent on clinical services requirements and the services requirements of selected equipment. Final configuration is to be confirmed at project level. ~ The clear area required on each side of the patient trolley for use of transfer aids (such as mobile hoists, patient slides, hover mats, etc.), the space for the trolley or wheelchair the patient is being transferred to, and the staff required to assist/complete the patient transfer, is to be considered and confirmed at project level. Work Health and Safety (WHS) policies and patient transfer devices that are intended to be used in the patient bay should be confirmed by the project team. ~ The weight capacity of recliners selected must be considered to suit a wide range of patient requirements. The recliner must also have the ability to lay completely flat. ~ Mobile duress coverage is to be assessed and planned at a department level and coverage is to meet local security and WHS policies as well as operational service requirements. ~ It is recommended that a dedicated power outlet, clearly separate from the medical services panel (MSP), is provided to support patient and visitor use for charging portable devices. Inclusion of integral USB outlets will depend on local ICT policies. ~ In some spaces, such as patient bays, a level of speech privacy of “confidential” would be recommended to protect sensitive patient information. However, due to clinical services requirements for patient care and observation, these spaces cannot be fully enclosed and therefore cannot achieve this level of speech privacy. The speech privacy rating of “not private” has been noted in relation to the elements of the physical environment that can contribute to speech privacy, however, operational approaches to maintaining confidentiality during discussions with patients and support persons must be considered. ~ Size, type and quantity of waste bins provided within the patient bay, including sharps bins, will be dependent on clinical service requirements, operational models for waste management (including separation of waste streams and frequency of waste removal) and local infection prevention and control (IPC) policies. It may be determined that bins for specific waste streams are to be located in a shared area between multiple patient bays and possibly brought to the patient bay as required. ~ Provision and extent of emergency/standby power and/or uninterruptible power supply (UPS) is to be confirmed to suit clinical services requirements and site conditions. Confirmation of power requirements is to be based on risk assessment considering the impact of a power outage on patient care/safety and medical equipment specifications. ~ Provision of cleaner’s power outlets is to be rationalised across the department and spaced in accordance with AS/NZS 3003. ~ Access to natural light and an external outlook is desirable. However, patient privacy must also be considered when determining window placement. Where high-level windows are provided to the bedhead wall of patient bays consideration must be given to the location of wall mounted items such as patient monitors. ~ The type, materiality and cleaning requirements of window coverings to external windows is to be confirmed at project level to suit local infection prevention and control (IPC) policies and risk assessments. Refer to Part D Section 6.4 for more information. | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | TRUE | FALSE | FALSE

## Items In Room Template
AusHFG Standard Components - File for Import
2026-03-31
No. of Standard Components = 44
Code | Template Name | Standard Component Set | Item List: Name | Item Number | Name | Quantity | Priority | Category: Name | Comment
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FIN | CLCN-041 | CORNICE: wall trim fixing, prefinished | 1 | 1 | Ceiling Cornice | square set cornice acceptable if flush set ceiling is provided
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FIN | CLTI-024.02 | CEILING: drop-in tiles, anti-microbial, acoustic, prefinished, 600 x 1200 | 1 | 1 | Ceiling Finish 1 | flush set ceiling is also acceptable
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ELGP-101 | GPO: single, wall mounted | 1 | 1 |  | to diagnostic set
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ELGP-131 | GPO: single, emergency power, wall mounted | 1 | 1 |  | low height, for patient recliner
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 2
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | ELGP-146 | GPO: single, emergency power, on services panel | 2 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ELGP-201 | GPO: double, wall mounted | 1 | 1 |  | for patient and visitor use to charge portable devices; inclusion of integral USB outlets is dependent on local ICT policies
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ELPR-071 | RCD: residual current device, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ELPR-081 | RCD: residual current device, emergency power, wall mounted | 1 | 1 |  | quantity and type to be confirmed to suit finalised power allocations
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | ELPR-083 | RCD: residual current device, emergency power, on services panel | 1 | 1 | Panel 2
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | ELSW-001 | SWITCH: light | 1 | 1 | Panel 1 | to ceiling recessed examination light; fixture may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FIDI-241 | DISPENSER: alcohol-based hand rub, wall mounted | 1 | 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FIHR-101 | BRACKET: suction bottle, wall mounted | 1 | 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FIHR-161 | BRACKET: storage basket, wall mounted | 1 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FIRT-051 | TRACK: curtain, privacy | 1 | 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FIN | FLSK-021 | SKIRTING: vinyl, integral with floor vinyl, coved | 1 | 1 | Floor Skirting
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FIN | FLVY-101 | FLOOR FINISH: vinyl, seamless, standard slip resistance | 1 | 1 | Floor Finish 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FQBS-101 | CHAIR: visitor, clinical areas | 1 | 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FQGE-101 | CURTAIN: privacy screen | 2 | 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FQGE-113 | BASKET: storage, for wall mounted panel, medium | 1 | 1 |  | type and extent of storage for consumables is to be confirmed to suit clinical services requirements, operational models for stock centralisation/decanting and local IPC policies
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FQWS-003 | BIN: sharps, clinical, medium | 1 | 1 |  | size to suit clinical services requirements and operational models for frequency of disposal; may alternatively be provided as wall mounted or on clinical trolleys that are shared across the unit and brought to the patient bay as required; solution to suit clinical services requirements and local IPC policies
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FQWS-031 | CART: sharps bin, clinical | 1 | 1 |  | sharps bin may alternatively be wall mounted or on a clinical trolleys that are shared across the unit and brought to the patient bay as required; solution to suit clinical services requirements and local IPC policies
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | FQWS-051 | BIN: general waste, 20L | 1 | 1 |  | size, type, quantity and location of waste bins will be dependent on clinical services requirements, operational models for waste management and local IPC policies
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ITCL-111 | LIGHT: nurse call indicator, ceiling mounted | 1 | 1 |  | outside curtain at foot of recliner; location to ensure visibility along paths of travel
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | ITCL-133 | BUTTON: nurse call, patient to staff call, with cancel, with handset connection point, on services panel | 1 | 1 | Panel 2 | may be combined on a single face plate with staff assist call button; located to support quick access by staff
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ITCL-181 | BUTTON: nurse call, staff assist, with cancel, wall mounted | 1 | 1 |  | may be combined on a single face plate with patient to staff call button; located to support quick access by staff
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ITCL-191 | BUTTON: nurse call, emergency, with cancel, wall mounted | 1 | 1 |  | located to support quick access by staff
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | ITCL-251 | HANDSET: nurse call, patient to staff call | 1 | 1 |  | with holder and cable management items as required
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | SER | LIFX-111 | LIGHT: examination, ceiling recessed | 1 | 1 |  | light switch located on MSP; may alternatively be provided as an articulated examination light with fixture mounted controls
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MGAS-022 | OUTLET: medical air, on services panel | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MGAS-062 | OUTLET: suction, on services panel | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MGFP-021 | FLOWMETER: medical air | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MGFP-041 | FLOWMETER: oxygen | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MGFP-061 | ADAPTER: suction | 1 | 1 | Panel 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | MMBE-091 | CHAIR: patient, recliner, clinical, electric | 1 | 1 |  | selected item to be able to lay flat
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | MMGE-191 | CANNISTER: suction bottle | 1 | 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FFE | MMGE-238 | DIAGNOSTIC SET: otoscope, ophthalmoscope and thermometer, wall mounted | 1 | 1 |  | configuration of diagnostic equipment to be confirmed to suit clinical services requirements
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 2 | to patient's left; content and configuration to be confirmed based on clinical services requirements and medical equipment selection
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | MSP | MMSP-051 | MEDICAL SERVICES PANEL: wall mounted | 1 | 1 | Panel 1 | to patient's right; content and configuration to be confirmed based on clinical services requirements and medical equipment selection
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FIN | WLFI-002 | WALL FINISH: paint, clinical areas | 1 | 1 | Wall Finish 1
PTB-E-AMT | Patient Bay - Emergency, Ambulatory Treatment | Emergency | FIN | WLPR-002 | WALL PROTECTION: bedhead wall panel, low height | 2 | 1 | Wall Protection